Carbon Dioxide for Pool pH Control

Subtitle: A Practical Guide for Trained Professionals

David Watson

The swimming pool bloke who reads a lot

Advance Review Copy - Not for Distribution

Note: Illustrations, form layouts and final layout pending

David Watson

Dw134.carnarvon@gmail.com

Unit 2 15 Carnarvon Street

East Victoria Park

Western Australia 6101

Mobile: +61 413 086 234

Publisher: David Watson Pool Consulting

Copyright © 2026 by David Watson

All rights reserved. No part of this book may be reproduced in any form without the prior written permission of the publisher, except as permitted by Australian copyright law.

ISBN (Paperback):

ISBN (eBook):

Printed in 2026

Publisher: David Watson Pool Consulting www.davidwatsonpoolconsulting.com

Cover design by Sue Knox

Illustrations by Sue Knox

Ingram Spark / Amazon KDP Print-on-Demand Edition

In preparing this handbook, AI tools have assisted with editing and verifying references across multiple international databases. All content has been carefully reviewed and edited for accuracy and reliability, informed by my four decades of field experience and current regulatory standards.

### Acknowledgement

I extend my sincere thanks to the early readers who reviewed the initial drafts of this book. Your thoughtful feedback, careful reading, and constructive suggestions made this work stronger and clearer. I am grateful for your support in developing this manuscript.

Contents

Part 1 — Foundations	8

1. What This Part Covers	8

2. Origins	9

3. Reader Skill Level and Scope of This Guide	13

4. Essential Safety Principles When Working With CO₂	15

5. Folklore	16

6. When CO₂ Is Less Efficient	17

(Higher Consumption Likely)	17

Excessive Use of Fountains	17

Aeration	17

Highly Turbulent Facilities	18

Open-Air, High-Wind Facilities	18

Toddlers Pools	18

7. When CO₂ is More Efficient (Apparently)	20

8. Runaway Total Alkalinity	22

Clarifying how acid and CO₂ lower pH	22

Why TA Behave Differently Under CO₂	23

Commercial vs domestic behaviour	23

(the real reason “runaway TA” shows up on site)	23

Bottom line for operators	24

9. Expensive to Manage	25

Part 2 — Installing a CO₂ System	26

10. How to Use the Install Chapters	27

11. Before Starting Installation	28

12. Storage	29

Bulk	29

Cylinder	29

Location	30

Retain	31

Ventilation	32

13. Sensors and Alarms	33

14. Auto Changeover and Regulator	37

CO₂ Regulator and Auto Changeover Gotchas	38

Gotchas Table	38

Regulator	39

15. Tube and Fittings	41

Sizing	42

Metric Tube Sizes and Nearest Imperial	43

Calculating Flow	43

Idea in one line	43

Work Out Tube and Fittings Needed	44

Fittings Equivalent Length Multiplier	45

Fitting Equivalent Length	45

Minimum (plastic) Tube ID (mm) (using LP ceramic diffuser)	47

Friendly rules of thumb	48

16. Protection	49

Colour	49

Labelling	50

17. Carbon Dioxide Gas Controller	51

18. Injection Point	53

Placement	53

Systems with Flows over 2000 litres per minute	54

Smaller Flow Systems	55

Velocity in metres per second by pipe and flow	56

19. Installation Complete	60

Part 3 — Operating a CO₂ Pool	61

20. Day‑to‑Day Operation in Plain English	62

21. pH Control	63

Science behind this	63

22. Correcting Total Alkalinity	67

Science behind this	67

Understanding “Total Alkalinity as Equivalent Calcium Carbonate”	68

Calculate Acid Dose	69

Example A — using HCl	70

Factor:	70

Dose per litre:	71

Total mass	71

Volume	71

Example B — Same scenario but H₂SO₄	72

Factor	72

Dose per litre	72

Total Mass	73

Convert kg to litres	73

How to Dose the Acid	73

23. Minimising Consumption	75

Science behind this	75

Reduce aeration	75

Use of Cover	76

Minimise splashing	77

Reduce wind	77

Decrease temperature	77

Raise pH	78

Lower TA target	78

Reduce chlorine levels	78

pH Controller Setting	78

Reduce Surface Disturbance	78

Plant Maintenance	79

24. CO₂ Consumption Calculator	80

Assumptions	80

How Sodium Hypochlorite Increases pH	81

Daily chlorine loss → daily CO₂ need (chemical equivalence)	82

Chlorine loss rate:	82

Account for CO₂ Injection Efficiency	83

Summary	84

25. Glossary	86

CO₂	86

pH	86

Total Alkalinity	86

Calcium Hardness	86

LSI	86

Hypochlorite	86

Diffuser	86

Venturi Injector	86

Bypass Contact Chamber	86

Specific Gravity	87

Equivalent Weight	87

Henry’s Law	87

Regulator	87

Aeration	87

Turbulence	87

Part 4 — Understanding the Science	88

26. Why the Science Matters (But Stays Practical)	89

27. Appendix: Langelier Saturation Index	90

28. Appendix: Henrys Law.	95

29. Henry's Law Meet Langelier Saturation Index	101

How does this help with Henry's Law?	102

Why is a swimming pool any different?	102

Part 5 — Technical Appendices & Tools	105

30. Quick Reference and Extras	106

31. Appendix: Calculating Tube Size Example	107

Step 1 — Area from tube size	107

Step 2 — Pressures we will use	108

Step 3 — Get a mean density (no stress)	109

Tiny ready-reckoner	111

Step 4 — Friction factor f (a quick practical choice)	111

Step 5 — Get the pressure “push” term	112

Step 6 — Mass flow in one line (Corrected Isothermal Compressible Form)	112

Step 7 — Velocity (so nothing is mysterious)	114

Step 8 — Optional quick safety check (Mach number)	114

Step 9 — If you need standard volumetric flow to match a datasheet	115

32. Appendix Painting Plastics	117

33. Appendix: Installation and Commissioning Checklist	119

Water Tests	119

Record Settings	120

34. Appendix: Start Up Steps	121

Step 1 — Do Nothing (Deliberately)	121

Step 2 — Speak to the normal Operator	121

Step 3 — Record, Don’t React	122

Step 4 — Allow the System to Find Its Balance	122

Step 5 — Return the Next Day	123

Guiding Principles	123

35. Appendix: Global Standards Crosswalk for CO₂ pH Control	125

Health Inspector Talking Points	126

36. About the Author	127

Contact and Support Information	128

A pool is not just water.

It is a series of interrelated systems.

It is our responsibility.

We own every drop until it's safe.

When a bather walks out the gate, they carry our standard with them.

They take it home, to work, to their communities.

Their safety — and the safety of everyone they touch — rests with us.

What This is About

Have you ever been confronted with a carbon dioxide pH-controlled pool with:

- Total alkalinity keeps increasing day after day, week after week, and it is blamed on carbon dioxide.

- pH that seems stable, but every week it is consuming more gas.

- Water that is grey toned, looks lifeless and dull.

This book explores these issues and gives you real-world practical guidance on how to correct them.

This book explores from:

- Suitability of the water body to the use of CO2 as pH donour

- Causes of runaway total alkalinity

- Installation from storage to diffuser

- And, how to operate a CO2 water body on an ongoing basis.

There are some theoretical underpinnings to the real-world guidance. This is not necessary to memorise; it is there to provide context and improve understanding of the why underneath the issues.

This book explains why pH behaves the way it does. The companion ORP/pH book explains how controllers respond to that behaviour.

Larger Pools Are More Forgiving

One important misconception to clear before embarking on the journey into CO2.

I have read and seen comments that a larger volume water body is more difficult to manage than a smaller volume.

Ever killed a goldfish?

Generally, as a child, most people would have gone to a shop and bought a small bowl and a goldfish.

Super excited you bring the bowl home, fill it with water and release your new pet into its home.

As a child, it was likely no one told you that a fish's stomach is the size of its eye. So, you loaded food into the bowl for your starving fish to eat.

Over a day or two, the goldfish would munch what it could, and the remainder of the food would float to the bottom of the tank and start to break down.

The water would go cloudy, and invariably, about day 2 or 3, the goldfish would be floating upside down.

This was likely your first death experience, and more importantly for our purpose, the first proof that smaller volumes are more difficult to manage.

If, on bringing the goldfish home, you had put it in your bathtub, and assuming you fed the same amount as in the small bowl, there is a good chance the goldfish would have lived.

The difference is simply maths.

Put it in perspective. Imagine for a moment there is a swimming pool. It is quite large, at 2,000,000 litres. Calculations done show a dosing requirement of 100 kg when the amount should have been 10 kg.

A 90 kg overdose of a chemical.

That 90 kg over the 2,000,000 litres would add about 45 mg/L to the parameter in question. Sure, it's annoying and will take a bit of time and product to fix, but most of the time, it is manageable.

Contrast that with a portable spa. Volume of about 1000 litres (sometimes less). In this spa, the same error, 1 kg instead of 0.1 kg of product, adds some 900 mg/L, this is drain the spa and start again. A much larger problem.

Large bodies of water dilute dosing mistakes. In other words, they are more forgiving of errors.

Small bodies concentrate them.

Larger water bodies are perceived to be more difficult to manage due to:

- High aeration features are often intended to impress rather than work

- Shallow interactive water sometimes dominate

- High bather loads relative to volume

- Strong wind exposure often resulting from architectural elements

- Regulatory targets that force specific levels of chemicals.

- Operational expectation inherited from smaller water bodies.

The reality is that if a larger water body is approached as a system, then the entirety of the issues all collapse into manageable chunks. CO2 is more common on larger water bodies. Perhaps not 2,000,000 litres but often 150,000 litres or more.

How to Read the Chemistry in This Book

For a more complete explanation, I have included chemical formulas.

It is important to realise that a reader does not have to remember or memorise them.

They are providing the complete back story. Wherever I can, I use simple chemistry to demonstrate the point and always include the equation in words as well. The chemical terms used are:

| Formula | Common Name | What it does in this book |
| --- | --- | --- |
| HOCl | Hypochlorous acid | The active, fast-acting sanitising form of chlorine |
| OCl⁻ | Hypochlorite ion | The weaker, high-pH form of chlorine |
| Cl₂ | Chlorine gas | The base form of chlorine; dissolves in water to form HOCl |
| NaOCl | Sodium hypochlorite | Liquid chlorine from a drum |
| Ca(OCl)₂ | Calcium hypochlorite | Granular or tablet chlorine |
| HCl | Hydrochloric acid | Acid most commonly used to lower pH |
| H₂SO₄ | Sulphuric acid | Alternative acid used to lower pH |
| CO₂ | Carbon dioxide | The gas that drives pH behaviour in pool water |
| H₂CO₃ | Carbonic acid | Transitional form of CO₂ dissolved in water; unstable |
| HCO₃⁻ | Bicarbonate ion | The main alkalinity buffer in pool water |
| CO₃²⁻ | Carbonate ion | Higher pH form of alkalinity |
| NaHCO₃ | Sodium bicarbonate | Raises total alkalinity |
| Na₂CO₃ | Soda ash / Sodium carbonate | Raises pH |
| H⁺ | Hydrogen ion | Determines acidity; directly affects ORP readings |
| OH⁻ | Hydroxide ion | Determines alkalinity; produced by salt chlorinators |
| H₂O | Water | — |
| CYA / C₃H₃N₃O₃ | Cyanuric acid | Stabiliser that protects chlorine from UV; reduces active HOCl |
| NH₂Cl | Monochloramine | Primary chloramine; irritant and disinfection byproduct |
| O₃ | Ozone | Strong secondary oxidiser; very short-lived residual |
| H₂O₂ | Hydrogen peroxide | Strong oxidiser used in AOP systems |
| •OH | Hydroxyl radical | Extremely powerful oxidiser produced by AOP; near-zero lifespan |
| HSO₅⁻ | Monopersulphate (MPS) | Non-chlorine shock oxidiser |

This table is here to refer to at any point. There's no expectation you'll remember it after one reading

# Part 1 — Foundations

What This Part Covers

This short section sets up the why.

It includes the origins of this book and the systems in it.

We clear the folklore, show where CO₂ does and doesn’t make sense, and explain the so‑called ‘runaway TA’ without blame or mystery.

If you’re deciding whether CO₂ suits your site, read this first, then skim back later when something on the pool deck behaves oddly.

Keep the mindset simple: pools aren’t static bodies— they are systems.

Origins

When I migrated to Australia in 1993, I already had a background in the swimming pool industry. But I also knew enough to recognise that a new country meant new water conditions, new regulations, and new expectations. I called the state health department and asked who the “chemical person” was for swimming pool chemistry. I was referred to Ty Webb, who at the time was the water scientist for the Government Chemical Laboratory.

Ty generously gave up his weekends to drive out to the outer northern suburbs of Perth to talk with me about swimming pool chemistry. In those sessions, he taught me about the role of carbon dioxide in pH control in all swimming pools and spas, particularly those with plastic equipment and fibreglass surfaces. Those lessons would later prove pivotal.

In late 1996, I was tasked with setting up the commercial division of our company — the part that would sell and service exclusively to commercial pool clients. I needed to find an edge in what was, at the time, a very closed market. My enquiries turned up two aquatic centres using CO₂ gas. I heard stories from the gas supplier about escalating gas consumption, and I recalled Ty’s explanations. I started thinking about how those principles applied to the specific needs of a commercial aquatic centre — the materials of construction, the equipment in the plant room, and the capabilities of the staff.

From this thinking, an idea formed: maybe the industry was applying CO₂ incorrectly, and maybe I could fix that in a practical way that staff would accept and adopt. Armed with nothing but an idea and a need, I picked up the phone.

The first centre I called was the one closest to my home.

“Hi, I’m David. Look, I have an idea how I can help you reduce your CO₂ consumption by at least 30%. I was wondering if this may be of interest.”

The reply was:

“I wish you had called last week. The CO₂ was removed this morning due to escalating TA and the cost of gas.”

It felt like I’d been sunk before I’d even begun. But having come this far, I made the next call.

“Hi, I’m David. Look, I have an idea how I can help you reduce your CO₂ consumption by at least 30%. I was wondering if this may be of interest.”

The response this time was completely different:

“What would you need from us to achieve this?”

I said, “I will need the pool closed to rebalance the pool water, and then for about eight weeks I’ll need to be responsible for any chemical additions of calcium chloride and hydrochloric acid. Staff will need to work with me. Once completed, they should be able to manage again without my help.”

The next question was, “How long would you need the pool closed?”

“About two to three days,” I said.

“Well, as it happens, we are scheduled to close for the entire Easter weekend. Will that be long enough, and what will this cost?”

“Yes,” I replied. “I think $3000 plus chemicals consumed.”

“Send me a quote.”

I spent the entire Easter weekend driving 35 km each way to the aquatic centre. I often arrived at 5:00 am and didn’t leave until 10:00 pm. I spoke with staff, took dozens of tests, and averaged six to eight tests across the two or three water bodies before making any dosing decisions. Once I was confident in the results, I began the treatment.

As best I recall, I initially added 1000 litres of hydrochloric acid to the pool water (this was appropriate for the size of the water bodies). The total alkalinity at the start was 240 mg/L, and the calcium hardness was around 100 mg/L. Before adjusting calcium hardness, I needed to first lower the total alkalinity to avoid forming calcium carbonate — a situation that can’t be reversed quickly without a massive acid dose. I had until Easter Tuesday.

By Easter Monday, I was looking at a completely different pool. The water that previously had a grey tinge and looked lifeless was now glistening, alive, and inviting. When the centre reopened, staff reported bathing load had increased within the week — not by a handful but by around 70%.

As promised, I monitored the water tests and logbooks daily. I phoned the appointed liaison each day to review results with them and explain my dosing decisions.

The immediate outcomes were:

CO₂ consumption dropped by more than two-thirds.

Aquatic centre revenue increased significantly.

An engineer active in the aquatics industry visited the centre with his daughter for swim squad training, contacted me, and this became a key moment that opened the industry to me.

Other aquatic centres soon began contacting us to install CO₂ systems on their sites.

For the next two or three years, we installed bulk CO₂ dosing systems at a rate of two to three complete systems per month. By the time the market was saturated (our state had only about one million people then), I was told we had more CO₂ installations than any other state in the country.

I’ve refined and reviewed my understanding continually since 1999. This book represents the culmination of that practical legacy from 1996–1999, combined with updated thinking and experience through 2023. I wrote my first drafts in 2023 and shared them with a select group, including Richard Falk, who kindly helped correct scientific errors and misconceptions. Those contributions remain as Appendix: Langelier Saturation Index and Appendix: Henry’s Law.

I have continued refining my thinking through 2026, and this edition reflects the knowledge accumulated to date.

I hope that anyone who applies the ideas in this book will see outcomes as remarkable as those I witnessed during that Easter weekend in 1997 — leading to safer dosing environments for aquatic centres and safer water for the communities they serve.

Reader Skill Level and Scope of This Guide

This guide is designed primarily for pool and spa professionals working with commercial aquatic systems, especially those involved with carbon dioxide dosing for pH control. However, the fundamental chemistry, physics, and practical principles discussed here apply to virtually any water body where pH control is essential—from backyard pools to large public or commercial facilities.

Whether you are a technician, operator, maintenance staff, consultant, or even an engaged homeowner seeking a deeper understanding, this book offers practical insights and clear explanations to help you work safely and effectively with CO₂ systems.

While the guide assumes some familiarity with basic water chemistry and pool equipment, it aims to be accessible to readers with a range of backgrounds. If you are new to these topics, the step-by-step approach and real-world examples will help you build confidence and knowledge.

Please note that safe handling of CO2 and chemicals requires proper training, adherence to local regulations, and respect for safety protocols. This guide supports professionals in making informed decisions but does not replace formal certification or licensing requirements.

Essential Safety Principles When Working with CO2

The procedures and recommendations contained in this guide involve handling pressurised gases, chemicals, and pool equipment, all of which carry inherent risks. Carbon dioxide (CO2) is a non-flammable but asphyxiant gas, and improper storage, installation, or operation can result in serious injury or death.

This guide is intended for trained professionals familiar with local regulations, safety standards, and best practices for handling pool chemicals and gas systems. Always:

- Conduct site-specific risk assessments before beginning any work.

- Use appropriate personal protective equipment (PPE), including eye protection and gloves.

- Follow manufacturer instructions and comply with all applicable laws and standards.

- Ensure proper ventilation in all areas where CO2 is stored or used.

- Never bypass safety devices or ignore warning signs.

- Seek expert advice or assistance if uncertain about any aspect of installation or operation.

The author and publisher disclaim any liability for injury, damage, or loss arising from the use or misuse of the information provided. This guide is educational and should not replace formal training, certification, or professional consultation.

Folklore

The moment you pick up this book or hear the phrase "carbon dioxide for pH correction" or similar, a few ideas likely spring to mind. Common are:

- CO2 creates runaway alkalinity

- Expensive to manage

- CO2 is difficult to install

- CO2 makes the water cloudy

- Is only for fancy resorts and councils

- CO2 can't keep up with heavy bathing use

- CO2  is slow to respond

- I am sure more can be added.

These are real events driven by misconceptions or misunderstandings.

In this book, I will look at these and show why they are not as concerning as they appear.

| Folklore | Chapter |
| --- | --- |
| CO₂ creates runaway alkalinity | 4 |
| Expensive to manage | 5 |
| CO₂ is difficult to install | 6.7.8.9.10.11.12 |
| CO₂ makes the water cloudy | 13,14,15 |
| Is only for fancy resorts and councils | All |
| CO₂ can't keep up with heavy bathing use | All, and specifically 16 |
| CO₂ is slow to respond | 3 |

When CO₂ Is Less Efficient

(Higher Consumption Likely)

All aquatic facilities already use carbon dioxide for pH control.

Consider this simplified equation:

HCl + NaHCO3 → NaCl + H2O + CO2

Hydrochloric acid + Sodium Bicarbonate → Salt + Water + Carbon Dioxide

This reaction is showing when acid is added to water that contains bicarbonate alkalinity, carbon dioxide is produced as part of the reaction. The pH reduction achieved by the acid is occurring through the carbonic acid/CO2 system, not from the acid itself.

Therefore, a facility cannot reasonably claim CO2 is unsuitable while continuing to rely on acid for pH control. The underlying chemistry is identical.

CO₂ works in every pool, but efficiency and gas consumption vary.

Facilities with high aeration or turbulence will use more CO2 to maintain the same pH setpoint. Indicators of higher consumption include the following.

[Figure code: FIG-01

Proposed title: CO2 Loss Spectrum by Feature (Low → High)]

Facilities With Continuous or Deliberate Aeration

Air features are common in some water bodies. But any feature that injects air into the water or breaks the water's surface will strip dissolved CO2, increasing demand. Examples include:

- Spray pads

- Fountains

- Watercannons

- Tipping buckets

- Interactive play features

This makes water spray pads and highly active shallow play areas generally poor candidates for efficient CO2 pH control. The gas is being continuously released back to the atmosphere as quickly as it is injected.

Spas

Spas present a similar challenge.

Heavy aeration from blowers and jets, combined with higher water temperatures, accelerates CO2 loss, leading to increased consumption and reducing control response.

CO2 can still be used. However, it is rarely the most practical pH control method for heavily aerated spas.

Highly Turbulent Water Bodies

Water bodies with sustained turbulence will require a higher gas input if CO2 is used for pH control. Examples include:

- Lazy rivers

- Rapid river attractions

- Wave pools

- Any pool designed to maintain constant surface disruption.

In each of these facilities, CO2 is being continuously stripped from the water. If the injection, contact time and control logic are not configured correctly pH correction may lag actual demand.

Open-Air, High-Wind Facilities

Outdoor pools exposed to strong, consistent winds behave like low-level aeration systems.

Rooftop pools, exposed coastal pools and shallow leisure pools with long beach entry are all particularly affected. Even with plant and equipment off, wind alone can drive significant water and CO2 loss.

One of the pools we built was located on the roof of a building, adjacent to the Swan River, with nothing but the river on two sides. The Swan is open all the way to the ocean and is wide. The winds were so severe that with nothing running, the pool water level would drop about 450 mm from wind loss overnight.

Toddler Pools

[Figure code: FIG-02

Proposed title: Why Toddler Pools Consume More CO₂]

Toddler pools require specific consideration.

These pools are typically:

- Very shallow, creating a high surface-to-volume ratio

- Warmer

- Sometimes equipped with spray features

- Subject to toddlers running about, causing surface agitation

Higher gas consumption would not therefore be a fault of the CO2 system. It is a predictable consequence of the pools physical characteristics and use.

When CO₂ is More Efficient (Apparently)

Some backyard pools use CO2 gas for pH control and reportedly operate without the runaway total alkalinity often reported in commercial pools. In many cases the owners report the system is working well.

The reason is not different chemistry.

Carbon dioxide will act identically in backyard or commercial pools. The only change between the two is the operating environment.

In comparison to commercial water bodies, domestic pools typically offer less:

- turbulence

- aeration

- bather load

- simpler automation dosing

- rigid TA target

- water feature behaviour

These differences assist in reducing CO2 loss and stabilising pH.

When Domestic Pools Show the Same Problems

Some backyard pools will show the same runaway total alkalinity seen in commercial water bodies. These pools are likely:

- Using continuous chlorine pH controllers

- Salt pools with TA>60mg/l

- Have high aeration features active

In these cases, the environment begins to resemble a commercial pool, and the chemistry responds accordingly.

Note: Backyard pools using salt chlorinators can, where the pool surface permits, be run at a TA of 30 mg/L. At this level, the pH becomes remarkably stable — in practice, a quarter cup of acid is often all that is needed to hold the pH in range. This is simply not an option in most commercial pools, where regulations mandate a higher TA floor, but it illustrates clearly that TA — not the choice of pH correction method — is the primary driver of pH stability.

The Role of Total Alkalinity

Where pool surfaces and equipment permit, domestic salt chlorinated pools can often operate at a total alkalinity near 30 mg/L. At this level, pH stability improves markedly, and acid demand is minimal.

This operating range is generally not permitted in commercial pools where regulations impose a higher alkalinity. However, the domestic example clearly demonstrates that total alkalinity, not the choice of pH donor, is the primary driver of pH stability.

The Governing Principle

CO₂ is chemically identical in all pools.

Differences in performance arise from how quickly CO₂ is lost to the atmosphere, not from the gas itself.

Runaway Total Alkalinity

This is one of the most troubling aspects of carbon dioxide for pH control. It is confusing for the technician and operator and is easily misunderstood.

In CO2 pools, the total alkalinity is seen to build and then, if left uncorrected, run away to extraordinary levels. Yet in acid pools, this same phenomenon is not seen.

Runaway TA in CO₂-managed pools is caused by continuous hypochlorite dosing, not by CO₂ itself. Here's why it shows up here but stays hidden in acid-managed pools.

Note: All pools that dose acid generate CO2 in the water as part of the normal acid–bicarbonate chemistry. That CO2 is what effectively lowers the pH. This can be expressed in the equation: HCl + NaHCO₃ → NaCl + H₂O + CO2 Hydrochloric acid + Sodium Bicarbonate -> Sodium Chloride + Water + Carbon dioxide In this reaction, we add acid to bicarbonate, releasing salt, water, and carbon dioxide. This is the reaction that occurs in every pool when acid is added. Carbon dioxide effectively reduces the pH of the water body. When carbon dioxide dissolves from water, the pH increases, requiring more acid.

Clarifying how acid and CO₂ lower pH

When a strong acid such as HCl is added, it supplies hydrogen ions (H⁺) directly, and the pH drops immediately.

In bicarbonate-buffered pool water, most of those H⁺ are taken up by the carbonate system:

HCO₃⁻ + H⁺ → H₂CO₃ → CO2(aq)

Bicarbonate + Hydrogen →Carbonic Acid → CO2 aqueous

CO2 dosing lowers pH via the reverse route: it first increases dissolved carbonic acid (H₂CO₃), which then releases H⁺ naturally.

CO2 → H₂CO₃ → HCO₃⁻ + H⁺

Carbon dioxide gas →Carbonic Acid → Bicarbonate + Hydrogen

The effect on pH is similar, but the delivery pathway is different:

Acid adds H⁺ directly; CO2 shifts the buffer equilibrium to generate H⁺ internally.

This distinction becomes important later when we talk about why TA behaves differently under CO2 control compared with acid control.

Why TA Behave Differently Under CO₂

The pathway difference shows up in total alkalinity (TA):

In acid-controlled pools, the acid neutralises the hydroxide byproducts that are generated with hypochlorite, so the TA rise is hidden.

However, in a CO2-controlled pool, CO2 does not neutralise those same hydroxides, so the TA rise becomes visible unless you add periodic acid to hold the TA setpoint.

Commercial vs domestic behaviour

(the real reason “runaway TA” shows up on site)

Domestic pools often dose chlorine intermittently, giving reactions time to reach their end points; overall, the system looks close to pH neutral. Backyard pool owners sometimes don’t have an issue.

Commercial pools dose chlorine continuously via automation to hold a compliant target (typical band 3.0–8.0 mg/L; we often run near 4.1 mg/L for headroom). In practice, continuous feed means the hydroxide load arrives continuously and faster than downstream reactions can consume it.

This results in CO2-managed commercial pools; TA appears to “run away.” It’s not caused by CO2; it’s driven by hypochlorite-introduced hydroxide. In an acid-managed pool, the same chemical is present, but the acid masks it by neutralisation.

Note: The worked examples use 80 mg/L because that's what regulations typically mandate; the appendix on LSI and Henry's Law shows why lower targets are chemically superior, and where your regulatory framework permits it, that's the better path.

Bottom line for operators

- Expect periodic acid doses to control TA in CO2 pools.

- CO2 is for pH; acid is still required to keep TA on target.

[Figure code: FIG-03

Proposed title: Why TA Appears to 'Run Away' with CO₂ Dosing]

Expensive to Manage

CO2  is not inexpensive as a product and needs appropriate storage vessels and alarms. Overall, the costs are comparable to those of maintaining an automated acid dosing system.

Acid systems often require special ventilation, and the dosing equipment requires more frequent servicing and replacement and in some places the cost of the acid is not that different to CO2.

# Part 2 — Installing a CO₂ System

How to Use the Install Chapters

Use these chapters as a build sheet.

Start with pre‑tests, then storage choices, then tube, sizing, protection and labels.

Finish with diffuser placement and a quiet commissioning checklist.

Don’t tune anything while you’re still learning how the site breathes. Record what you do. Small, neat changes beat big, clever ones.

Before Starting Installation

Before starting an installation, establish the baseline chemistry of the incoming water used to fill the pool.

The tests required would be:

- Free Chlorine

- Total Chlorine

- pH

- Calcium Hardness

- Total Alkalinity

- Cyanuric Acid – should be nothing in the incoming water source.

- Total Dissolved Solids

- Plus any additional tests specific to your location.

Record these readings. If the water supply in the area is known to change regularly, consider collecting this data daily, weekly or monthly. For example, in our region, the water supply used to be supplied as a blend of ground and dam water. This resulted in a varying mix of incoming mains. In this instance, I would collect samples once a week for 4 weeks and average the results to get a better idea of what the water body may expect.

Complete a water test on the water bodies as they are. Again, record all the above parameters.

These baseline values will be referenced throughout the pH-control and operational chapters.

Storage

[Figure code: FIG-04

Proposed title: CO₂ Storage Options at a Glance]

Bulk

In Australia, it is simple enough to call the gas supply company and arrange to meet on site or have them come and inspect the site to determine the best installation point for their vessel and equipment. Typically, the gas company will install the bulk vessel and run a line to a regulator, where we can pick up a supply.

Other parts of the world may have a different approach.

The following are universal principles:

- Gas detection is mandatory in enclosed spaces.

- CO2 storage must be ventilated

- Regulators must be protected from moisture.

- Changeover manifolds must be sized for the expected draw.

- Bulk tanks require supplier involvement.

- Cylinders require secure anchoring and separation from ignition sources.

These are true everywhere.

Note: For all enclosed spaces, a sniffer or gas detection device is mandatory. This should be installed in the lower part of the room, as the gas is heavier than air. Always refer to the manufacturer's instructions and the local regulations for the specific requirements.

Cylinder

Cylinder storage requires more planning. There is no reason it can't be used; it is a good idea to complete the consumption calculations in Chapter 22 first to get an idea of the daily gas consumption. It may show that cylinders are not really viable.

Location

In Australia, CO2 is classified as a Class 2.2 non-flammable, non-toxic gas. It is an asphyxiation hazard, so standard derived separation distances relate to:

- preventing cylinder heating

- preventing mechanical damage

- preventing cross-hazards with other gas classes

The Australian Standard AS 4332:2004 lays out the following separations:

| Metre |  | Note |
| --- | --- | --- |
| 0 | From ignition sources | CO2 is non-flammable no minimum distance required for ignition-source separation |
| ≥ 1 | From heat sources | Boilers, steam lines, hot surfaces, or radiant heat. Cylinders must be kept clear of heat sources that could raise cylinder temperature above safe limits. |
| 3 | From incompatible gases | CO2 (Class 2.2) must be separated from: • Class 2.1 flammable gases • Class 2.3 toxic gases • Class 5.1 oxidisers Note that the 3m can be measured around a 30-minute fire-rated wall |
| N/A | From property boundaries and public areas | • No fixed minimum distance from boundaries • But cylinders must be protected from vehicle impact and located where a leak cannot accumulate in pits, basements, or confined spaces. |

As CO2 is an asphyxiant, adequate ventilation is required.

The above are the AS-mandated distances and are to be observed on installation. Others are likely a good idea. Consider:

| Metric | Suggestion |
| --- | --- |
| 3 metres | Minimum distance from door or window openings into plant rooms or other public spaces. |
| Avoid | Areas with pits or balance tanks below floor level. |
| Avoid | Adjacent to sub-surface workspaces, e.g. underground plant rooms. |

As CO2 is heavier than air, it will accumulate in lower spots and areas first.

Retain

Gas cylinders are pressurised vessels. If the valve is knocked off through physical impact, the cylinder can become a lethal projectile. To help prevent this, cylinders should be:

- Placed on a level, solid base.

- Chained or strapped securely to a wall, bracket, or solid post.

- Protected from impact on all sides (e.g., bollards, cage, guard rails).

- Protected from weather extremes, especially heat and direct sun.

- Never transported lying down unless they are fully restrained so they cannot roll or move.

Ventilation

As mentioned, CO2 is an asphyxiant. It is worth highlighting ventilation for this reason.

Ideally, the installation location should be outdoors, secure and away from any chance of entry into the normal workspace.

Regardless, additional ventilation is likely a good idea in spaces adjacent to or where gas is being fed through for pH control.

CO2 may be visible briefly as a cold fog when released. As it warms, it becomes invisible and odourless

Reminder: CO2 sensors are typically mounted 150–300 mm above the finished floor near likely leak points. Always follow the detector manufacturer's instructions and the authority having jurisdiction.

Sensors and Alarms

Gas detection is a life-safety control, not an optimisation tool. The purpose of detection is to alert occupants to dangerous accumulation before symptoms occur.

For any outdoor installation, a gas sniffer alarm is not normally required by Australian Standards. However, for any installations inside a plant room or similar, a gas detection system and alarms are mandatory.

Gas detection systems in plant room locations are to be:

- No more than 300 mm above the finished floor level

- Providing adequate monitoring for the entire plant room area, including any pits, balance tanks, and similar below-floor areas.

For pool plant rooms where the storage is installed outside and the tubes are passing through the room to the diffuser, it is a good idea to fit an extra gas sniffer alarm.

The table below lays out minimum suggestions for gas detection. The table includes cellars, as CO₂ is often used in bars. For our purpose, the cellar room is any space below the floor. An open balance tank, a split-level plant room and others are examples of these spaces.

| Room Dimensions / Characteristics | Typical Description | Suggested Number of CO₂ Sensors | Placement Notes |
| --- | --- | --- | --- |
| < 10 m² (Small room) | Small cellars, small cool rooms, small plant rooms | 1 sensor | Mount low (≈ 600 mm above floor). Place as close as practical to cylinder(s) or leak source. |
| 10–25 m² (Medium room) | Standard cellar, medium plant room | 1–2 sensors | Use 1 sensor if the room is clear and unobstructed; use 2 if shelving or partitions create dead zones. |
| 25–50 m² (Large room) | Large cellars, larger indoor gas rooms | 2 sensors | Place sensors on opposite sides of room, both low-mounted. Avoid placing both near doors/vents. |
| 50–100 m² (Very large room) | Extended cellars, larger plant rooms | 2–3 sensors | Space sensors evenly across room footprint. Prioritise corners or low-lying pockets where CO₂ can settle. |
| > 100 m² (Complex / industrial room) | Multi-zone plant rooms, long corridors, split areas | Minimum 3 sensors, often 4+ | Treat each sub-area or separated zone as needing its own detector. Add sensors near CO₂ piping manifolds or regulators. |
| Room with heavy shelving, pillars or machinery | “Broken up” rooms with poor airflow | +1 extra sensor beyond size-based number | Treat obstructed sections as separate zones. CO₂ settles and pools around obstacles. |
| Room with multiple CO₂ cylinders separated by distance | Two ends of a room, or two distinct storage points | 1 sensor per cylinder zone | Each cylinder zone should have its own sensor due to local pooling patterns. |
| Room with gas lines entering from outside | Dosing lines, Beer gas systems, manifold lines | 1 sensor near entry point + standard sensors | Detects leaks from piping, not only cylinder storage. |
| Any room with a cool-room attached | Common in hospitality sites | 1 sensor in cellar + 1 inside cool-room | Treat cool-rooms as separate atmospheres. |

Pool plant rooms are not a simple bottle store. There are pieces of equipment, bracketing, pipework, and a raft of other physical objects. This may interfere with normal sensor operation if the dosing lines are intermixed with other equipment. In plant rooms, consider additional sensors as needed.

Auto Changeover and Regulator

For bulk storage, the regulator is usually installed as part of the gas company's service.

For cylinders, a regulator is usually installed by the installer as part of the automatic changeover system.

An auto changeover head for CO₂ is simply a dual-inlet pressure regulator with a small internal shuttle valve that compares the inlet pressures. Whichever cylinder has the higher pressure automatically becomes the active supply. As the primary cylinder empties, its pressure drops once all liquid CO₂ has boiled away.

[Figure 21- AutoChangeover]

CO2 boils as the gas is drawn off to correct the pH. That is, CO2 is liquid under compression, and as the pressure is reduced, the liquid ‘boils’, releasing the gas for our use.

Just because the liquid has boiled away sufficiently to reduce pressure, the cylinder may still contain some liquid. Always treat cylinders, empty or full, as though they are full.

When the inlet pressure falls below the regulator’s differential threshold, the shuttle moves and the reserve cylinder takes over without interrupting the gas supply.

If you’ve ever seen how a Kreepy Krawly propels itself using nothing more than pressure differences and a small internal hammer, the shuttle valve in an auto changeover head works on the same principle. The side with greater pressure wins; when that pressure drops, the shuttle flips.

A colour window or arrow on the front of the module mechanically follows the shuttle's position, indicating which cylinder is currently in use. The system needs no power, no sensors, and no calibration—just basic plumbing and correct tightening of fittings.

CO₂ Regulator and Auto Changeover Gotchas

This subsection summarises the practical gotchas that can catch technicians when working with CO2 cylinders, regulators, and auto-changeover heads.

Gotchas Table

| Gotcha | Explanation |
| --- | --- |
| CO2 is right‑hand threaded | Australian Type 30 fittings use 0.860” WHIT, 14 TPI right‑hand threads, not left‑hand. |
| Washer required for Type 30 | Flat‑face sealing requires nylon, fibre, or metal‑bonded washers between the regulator and valve. |
| No PTFE tape | Tape must not be used on cylinder valve threads because sealing occurs at the washer, not the thread. |
| Don’t mix standards | Type 30, CGA‑320, DIN/BS CO2 threads are not interchangeable and can’t be forced to fit. |
| Washer reuse limits | Fibre washers are single‑use; nylon/metal washers may be reused if undamaged. |
| Over‑tightening the nut | Too much torque damages the regulator seat or crushes the washer; firm compression is enough. Try hand-tight, then a quarter turn with a wrench. This is usually sufficient to create a positive seal on the washer/O-ring without crushing or distorting it. |
| Confirm correct stems & nuts | Ensure Type 30 stems/nuts are used, as Type 10/50 appear similar but won’t seal correctly. |
| Do not mix BSP & NPT | Thread systems differ; mismatches can cause leaks or thread damage unless proper adaptors are used. |
| Autochangeover primary assignment | Set one side as primary and reset the indicator after replacing cylinders. |
| Pressure rating mix-ups | Use high‑pressure‑rated components upstream; many hobby fittings are only safe post‑regulation. |

Regulator

The regulator on a CO2 storage system performs two key functions.

First, it provides an indication of the pressure remaining in the current tank—whether that is a bulk vessel, a cylinder connected to an automatic changeover manifold, or a single standalone cylinder. CO2 in the cylinder is stored as a liquid under pressure. As it boils, it produces the gas used by the dosing system. Because the pressure is governed by the liquid–vapour equilibrium, the storage pressure acts only as an indicator of remaining volume, not a literal measurement. The gauge will show near-constant pressure with only small deviations—until the liquid is almost gone, at which point the pressure drops rapidly.

[Figure 22 – Regulator]

The second gauge displays the line, or delivery, pressure. This is typically adjustable via a control knob on the regulator.

If the delivery pressure is set too low for the demand of the water body, the system may draw gas through the regulator too rapidly or continuously. Under these conditions, significant Joule–Thomson cooling can occur.

The Joule–Thomson effect may be observed as ice forming around the regulator. It can also appear around the solenoid valve in the carbon dioxide gas controller. Some manufacturers offer heated regulators to mitigate this, and in some climates, this may be necessary.

However, in warmer climates, simply slowing the gas draw off is sufficient to reduce the icing occurrence.

Tube and Fittings

In the pool industry, the more common materials are PVC pipe and some dosing tubes that are usually PVC or cross-linked polyethylene. Usually, these are supplied as part of the chemical control. Some suppliers of chemical control for CO2 don’t supply tubes or fittings. In that case, this small introduction will assist.

With CO2, material choices are wider than with other chemicals. For cost-effective installation, we use a nylon 12 tube. Talk to your local hose supplier, they will have some suitable tube.

Broadly, tube fittings come in two styles: the push fit and the knurl and nut. These work differently.

The push fit generally has a collet that is pressed down to release the tube.

[FIG-23 – push fit fitting]

As the name implies, the tube is cut square and pushed into the fitting.

[FIG-24 – push fit fitting cut away]

On bottoming out against the tube, the O-ring provides the seal, and the collet holds the tube in place.

This type of fitting is faster to use than others and improves the installation time. However, before using, always check with the manufacturers that their fitting is suited to your specific installation requirements, including chemical compatibility and the likely pool parameters.

Another type of tube fitting utilises a knurl.

[FIG-25 – Knurl Type Fitting]

These fittings are more likely to be of metallic construction. If using metals, it is very important to check the compatibility with all the pool chemicals present. As these fittings are typically used industrially, they are usually available in an alloy suitable for our use.

Note: Always discuss with the tube supplier the specific application, tube and fittings to ensure they are compatible not only with the chemical but also with each other. Some tube fittings, for example, are specifically designed to work with stainless steel tube; if nylon 12 tube were used with these fittings, the tube would be severed. The supplier will know which tubes and fittings work together.

These work differently from push fit. However, if in a hurry, they can be used similarly with experience.

[FIG-26 – Knurl Fitting Cutaway]

The nut is loosened, and the tube can be inserted into the fitting. Once bottomed out, the nut can be tightened, sealing the tube in place. Always follow the manufacturer's instructions. This book is not meant as a replacement; it is a general guide.

Note: The tube used for CO2 is not always compatible with other chemicals. Always check materials for suitability before use.

Sizing

Industrial tube and hose suppliers use different sizing conventions for metric and imperial. Just because your location is primarily metric doesn’t mean you will always buy metric tubes. Commonly, ¼-inch nylon 12 tubing is our go-to for CO2 dosing.

However, the sizing differs. Imperial sizing is typically outside diameter only. ¼ inch is a ¼ inch external tube. On the other hand, metric tube is sized external followed by the internal measurement 8 x 5, meaning 8 mm external and 5 mm internal.

Metric Tube Sizes and Nearest Imperial

| Metric Tube (OD × ID) | Nearest Imperial | Notes |
| --- | --- | --- |
| 5 × 3 mm | ~3/16" (4.76 mm) | Light-duty gas/dosing lines. |
| 6 × 4 mm | ~1/4" (6.35 mm) | Very common pneumatic/dosing size. |
| 8 × 5 mm | ~5/16" (7.94 mm) | Common CO2 feed line in the pool industry. |
| 10 × 6.5 mm | ~3/8" (9.53 mm) | General-purpose gas/liquid transfer. |
| 12 × 8 mm | ~1/2" (12.7 mm) | Used for long runs or higher flow. |
| 15 × 11 mm | ~5/8" (15.88 mm) | Less common but used in higher-capacity systems. |

[Figure code: FIG-05

Proposed title: Tube Size Translation: Metric OD×ID vs Imperial OD]

Calculating Flow

For detailed calculations, refer to Appendix Calculating Tube Size Example. The full maths is laid out there. Please take the time to look at the maths. I don’t assume anyone is good at maths, as I am not. I make every effort to make math clear and as easy to follow as possible.

Idea in one line

A longer, skinnier tube slows gas more. A bigger inside diameter or a shorter run gives you more flow for the same regulator setting.

Work Out Tube and Fittings Needed

One practical way to estimate pipe length is to pace the distance. For most adults, a normal step is approximately 150–300 mm, while a long stride is close to one metre. Elevation changes can be estimated relative to your own height.

Alternatively, measure a repeating surface element, such as a paver and count the number of units. For example, a 450 mm paver across 14 units equals 6.3 metres.

Where accuracy matters, use a measuring tape, scale directly from drawings, or apply another precise measurement method.

Looking at the installation record the likely fittings post regulator:

| Fitting | Count |
| --- | --- |
| 90° standard elbow |  |
| Swept long-radius bend |  |
| Tee (straight through) |  |
| Tee (branch take off) |  |
| Ball Valve (full port) |  |

This is the list of the most common fittings used in CO2 installations. If the specific install uses another fitting instead, simply estimate as the closest fitting; for example, a 45 standard elbow is likely closest to a swept long radius bend.

Now, using the tables below and your count of fittings, you can estimate the equivalent length. Note that this table is generic and not specific. If your fitting supplier provides  equivalent length data, use that instead of this method.

[Figure code: FIG-06

Proposed title: What 'Equivalent Length' Means (Visual)]

Fittings Equivalent Length Multiplier

| Fitting Type | Averaged Multiplier (× D) | Notes |
| --- | --- | --- |
| 90° standard elbow | 40 D | Midpoint of 30–50D range |
| Swept long-radius bend | 18 D | Midpoint of 15–20D range |
| Tee (straight-through) | 40 D | Middle of typical 20–60D range |
| Tee (branch take off) | 80 D | Middle of 60–100D |
| Ball valve (full port) | 30 D | Midpoint of 20–40D |

Fitting Equivalent Length

| Tube ID (mm) | 40D Elbow (m) | 18D Swept Bend (m) | 40D Tee (straight) (m) | 80D Tee (branch) (m) | 30D Ball Valve (m) |
| --- | --- | --- | --- | --- | --- |
| 4 mm | 0.160 | 0.072 | 0.160 | 0.320 | 0.120 |
| 5 mm | 0.200 | 0.090 | 0.200 | 0.400 | 0.150 |
| 6 mm | 0.240 | 0.108 | 0.240 | 0.480 | 0.180 |
| 8 mm | 0.320 | 0.144 | 0.320 | 0.640 | 0.240 |
| 10 mm | 0.400 | 0.180 | 0.400 | 0.800 | 0.300 |

Before finalising the pressure drop in the fittings, skip ahead to the Minimum Tube ID table, and using your likely closest length, select a likely tube size to use. Our length is 27 metres, as this is above 25, we select the tube ID corresponding to 30 m. We nominate a gas regulator pressure of 300kPa.

The equivalent length method provided here is conservative. Tube sizes are selected such that gas velocity does not exceed 15 m/s under expected operating pressures. This provides margin against minor installation variations, additional fittings, and normal regulator adjustment. Where installations fall outside these assumptions, verify using the full flow method in the Appendix.

Having decided from the Minimum tube ID, our tube is 5 mm internal. The following is a worked example:

| Fitting | Count | Fitting Equiv. Length | Count x Fitting Equiv. L. |
| --- | --- | --- | --- |
| 90° standard elbow | 4 | 0.200 | 0.800 |
| Swept long-radius bend | - |  |  |
| Tee (straight through) | - |  |  |
| Tee (branch take off) | - |  |  |
| Ball Valve (full port) | 1 | 0.120 | 0.120 |
| Total |  |  | 0.920 |

In our worked example, there are only a few fittings; in a more complex install this list could grow.

Add this length, 0.92 m, to our tube length. Our tube length on site was, say, 27 metres, so the total is:

27 + 0.92 = 27.92 metres. Round up to 30

This verifies our 5 mm tube size based on a gas regulator pressure of 300kPa.

[Figure code: FIG-7

Proposed title: How to Pick Tube ID in 3 Steps]

Minimum (plastic) Tube ID (mm) (using LP ceramic diffuser)

|  | Length m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Reg P out (kPa) | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 60 | 70 | 80 | 90 | 100 |
| 100 | 6 | 6 | 6 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 |
| 150 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |
| 200 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 8 | 8 | 8 | 8 |
| 300 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 |
| 400 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 |

This table shows the minimum internal diameter for smooth-bore polymer tubing, sized to keep CO₂ gas velocity below 15 m/s.

If using metallic, rubber, corrugated, or any non-polymer tubing, the internal roughness and friction factor will differ, so you must use the Appendix method to calculate the correct Reynolds number, friction factor, and resulting minimum tube ID.

Friendly rules of thumb

- Bigger ID or shorter length → more flow with the same regulator setting.

- If the response is slow, first try a larger tube or shorter run before changing controller tuning.

Protection

Encase the tube in conduit. Electrical conduit is a good choice, it comes in convenient sizing for inserting the tube and is readily available, easy to get mounting brackets for, lightweight and most importantly, protects the tube inside.

Typically, we will use 25 mm conduit.

For corners, we use the flexible conduit in place of the bends. It's easier to use a flexible conduit as a tube may be pushed into loops, and similarly, this product will bend to accommodate.

For termination of the conduit, we use a cable gland adaptor.

This is a great idea for protecting the tube and doubles to contain the gas if there is a leak providing an additional safety point. However electrical conduit is colour coded and the colour coding is not for CO₂ gas. Our solution is to paint it.

Colour

In Australia, there is a standard on the colours of conduits and pipes. This standard is AS 1345-1994 - Identification of the contents of pipes, conduits and ducts. These standard lays out the colours to use for any pipe, conduit or duct based on its content. Check your region for the appropriate requirements in your area.

Under AS 1345, the colour for CO₂ gas is Yellow Ochre / Sand. Again, there is another standard that has a code for the colour, this is AS 2700:2011 colour standards for general purposes. Under AS 2700:2011, the colour code is Y44.

If you want to be pedantic, go to a dedicated paint store and ask them to make a batch of AS 2700:2011-compliant paint colour code Y 44. They will usually be able to help.

The issue with this colour coding is that chlorine gas lines are also coloured to Y44. My concern with this is that the CO₂ line could, in an emergency, confuse responders into thinking they are dealing with a chlorine rather than carbon dioxide gas. After all, swimming pools are not bars where CO₂ is expected.

To work around this, we use a sand colour for CO₂ lines rather than the AS 2700:2011 Y44 colour specified. Along with labelling, this assists in clearly identifying the CO₂ lines within the plant.

Labelling

Always label the conduit with content. We get a label printed specifically to suit it is a simple label:

< Carbon Dioxide Gas >

We trim the arrow off one of the ends to show the normal flow direction.

When ordering the labels, ask for vinyl outdoor permanent placement material. This is waterproof and less likely to fade or be damaged in a pool plant room.

AS 1345 does specify the distance between labels in a way. In summary, the labels must allow identification from a normal working position. It includes:

- At or near any valves

- At changes of direction

- At or near any junction

- At reasonable intervals on straight runs

For the CO₂ conduit, we will typically label about every 2.5 – 3.0 metres. The exception is where we are passing through a wall, bulkhead, doorway, or similar. In that case, we will label either side of the wall.

Carbon Dioxide Gas Controller

Various commercial pool-dosing companies manufacture versions of this device. They are relatively simple, broadly consisting of a solenoid, a gas rate meter and an on/off switch.

[FIG-27 – Carbon dioxide gas controller]

Internally, the device is not complex; we will cover this later.

For installation, we use a simple rule. The device in this case has a switch and a rotary knob for adjustment. Some people are tall, and some aren’t. The device may need adjustment, so the installation height must be accessible to everyone.

Install between the knee and shoulder height of the average person, as this device has a rate meter and is likely to be viewed; install it toward the upper side of this unofficial rule.

Note: If the item in question doesn’t require frequent adjustment or reading, install it at a height suitable for the work. For example, a valve that must be adjusted to maintain flow through a heater may only need to be set at start-up. This valve can be, and probably should be, installed with ladder-only access.

Always install the CO₂ controller near the pH controller. CO₂ is a pH-correction donor; therefore, this is logically where to install it. As with a dosing pump, the pH controller can likely be used to manually engage the CO₂ controller for testing. It's helpful, from an operational perspective, to be able to stand at the pH controller, switch to manual, and glance at the CO₂ controller to confirm it is running properly.

Like other similar devices, do not install the CO₂ controller where it is subject to:

- Extreme heat

- Extreme cold

- Extreme dust

- Extreme humidity

- Overhead risks such as fluids

- Objects falling on it

The CO₂ controller needs electrical power. Depending on your pH controller, this power may be supplied directly by the controller. Alternatively, a local general-purpose outlet may be needed where the pH controller uses a signal cable to the CO₂ controller. Always get electrical work completed by licensed electricians.

The tube connects to the CO₂ controller using either a specific fitting or, in some cases, a push-fit fitting included in the controller itself.

Similarly, the tube is removed from the CO₂ controller and routed to the injection point.

Be aware that if CO₂ demand is extended or high, ice can form on the solenoid. This can freeze the solenoid open, which in turn increases demand, leading to more Joule-Thomson cooling. If the pool's pH is plummeting or sitting around 6.1, then this is the most likely issue. Remove the cover on the CO₂ controller. If the solenoid is covered in frost like ice, this is likely the issue. Use a heat gun or similar device to melt the ice and heat the solenoid; it will close.

Injection Point

I dislike calling it an injection point. It’s usually a diffuser or venturi injector. But it's more common to call it the injection point. In this book, I will use the term "diffuser".

For CO₂ gas, the job of the ‘injection’ point is different to other chemicals. This is the point at which the gas is introduced into the water. Ideally, the gas will be introduced as a fine mist rather than as a surge of chemical, as may happen with chlorine or acids.

Note: CO₂ is still a chemical, albeit a different form than the more common liquids we use daily. Like any chemical, the diffuser should be installed at least 350 mm from the chlorine injector.

Use a ceramic diffuser by choice. This, in my opinion, provides the best possible interfacial area. What I mean is that the diffuser's surface area is relatively large, and the bubbles formed are often microscopic, leading to more direct and immediate absorption of CO₂.

[FIG-28 – Ceramic Diffuser]

Note: Fine bubbles from the return to the pool closest to the plant room are likely CO₂ gas that has not been successfully absorbed.

Placement

Location of the ‘injection’ point is as critical as the choice of injector.

The following are factors that influence the diffuser placement:

- Bubble size. For all this text, I am assuming an LP ceramic diffuser. If using a different diffuser, the bubble size needs to be considered.

- Gas hold up. This is the mixing zone around the immediate injection point.

- Hydraulics. The mixing shear and turbulence.

- Temperature, warmer water dissolves the gas faster.

- Equilibrium point. This is perhaps the least understood, so it is worth taking the time to explain.

“Equilibrium” in this context means the point where the amount of dissolved gas in the water is balanced by the amount of that gas leaving the water into the air. At equilibrium, the rate of gas dissolving equals the rate of gas escaping.

Swimming pools almost always operate above the natural equilibrium concentration of CO₂ because people, heaters, and turbulence drive CO₂ out of the water faster than it can be replenished from the atmosphere.

This is important for pH, alkalinity behaviour, and aeration effects, and it is explained in more detail in the operational chapters later in the book.

An ideal location could be in line with, or just before, a highly turbulent area of the pipe works. Examples of highly turbulent areas include an elbow followed by a valve followed by another elbow; the pump itself is highly turbulent; and discharge from the pump can be turbulent if the valves or other devices downstream of the pump are installed before the flow-stabilisation region. I am sure that looking at the installation will reveal other areas.

[Figure code: FIG-10

Proposed title: Where NOT to Install a CO₂ Diffuser]

Systems with Flows over 2000 litres per minute

One of these areas is markedly better than the others. In an ideal installation, place the CO₂ injection just before the inlet to the pump. I do not mean in front of the hair and lint pot. I mean, after the hair and lint pot and just before the pump.

This means the microbubbles are introduced into the pump impeller's eye. The gas and water are thrashed about within the volute and will have the best chance of complete absorption, usually before they leave the pump.

[Figure code: FIG-8

Proposed title: Best Injection Location on High-Flow Systems]

The amount of CO₂ gas injected is usually very small. It is so small that at any time it won’t create an issue for the pump.

Smaller Flow Systems

For smaller flows, the pumps usually have hair and lint pots moulded onto the pump front. The opportunity to fit the diffuser between the hair and lint pot and the impeller is substantially reduced. An alternative location needs to be considered.

In this instance, the velocity of the water in the pipe work needs to be considered. Whilst this book is not about pipe work velocity, the equation is:

V = Q / A

Where:

V=velocity

Q= quantity

A = area

A worked example is helpful to understand this better.

We are trying to find V or velocity.

The flow rate from the manufacturer's pump curve is around 500 L/min.

The pipe diameter is 80 mm.

Q = 500 L/min or 8.33 l/s, which needs to be converted to cubic metres per second 0.00833 m3/s

A = πr2  for a pipe of 80 mm diameter, the radius r is 40 mm. However, we need this expressed as part of a metre. So, it is 0.040 m

A = π x 0.0402 = π x 0.0016 = 0.00503 m

Notice that both units are expressed as metres. This is important mathematically; the two need to be the ‘same’ units. Now we have:

Q = 0.00833 m3/s

A = 0.00503 m

Using our formula for velocity, we can work this now:

V = Q / A

V = 0.00833 (m3/s) / 0.00503 (m)

V = 1.65 m/s

For quick reference in the field. Find the pipe diameter and the flow in litres per minute:

Velocity in metres per second by pipe and flow

| L/min | 40 mm | 50 mm | 80 mm | 100 mm |
| --- | --- | --- | --- | --- |
| 300 | 0.994 | 0.636 | 0.248 | 0.159 |
| 350 | 1.160 | 0.742 | 0.290 | 0.185 |
| 400 | 1.326 | 0.848 | 0.331 | 0.212 |
| 450 | 1.492 | 0.954 | 0.373 | 0.238 |
| 500 | 1.657 | 1.061 | 0.414 | 0.265 |
| 550 | 1.823 | 1.167 | 0.455 | 0.291 |
| 600 | 1.989 | 1.273 | 0.497 | 0.318 |
| 700 | 2.321 | 1.485 | 0.580 | 0.371 |
| 800 | 2.652 | 1.697 | 0.663 | 0.424 |
| 900 | 2.984 | 1.909 | 0.746 | 0.477 |
| 1000 |  | 2.122 | 0.828 | 0.530 |
| 1200 |  | 2.546 | 0.994 | 0.636 |
| 1400 |  | 2.970 | 1.160 | 0.742 |
| 1600 |  |  | 1.326 | 0.848 |
| 1800 |  |  | 1.492 | 0.954 |

The lower the velocity, the less turbulent the pipe is likely to be.

The typical time required for the CO₂ to be absorbed into the water is from 5 to 35 seconds. Using the velocity table, the amount of straight pipe can be worked out for this time.

A worked example helps make this clearer.

Pump manufacturers flow curve shows 550 litres per minute at the current pressure.

Pipe fitted is 50 mm.

From our table, the velocity is 1.16714 m/s.

Therefore, in 5 seconds, the equivalent straight length of pipe is:

5 x 1.16714 = 5.837 metres

And in 35 seconds, this is

35 x 1.16714 = 40.849 metres

Both are substantial in a small plant room and may likely be impractical. However, there is another way to make it work.

Our options are:

- Increase turbulence

- Decrease pipe diameter

- Increase pipe length (if possible)

- Decrease bubble size

- Make water warmer

In practice, a bypass is likely a better solution.

This is a different bypass from what you may be thinking. This is a bypass for the express purpose of dissolving CO₂ gas only.

The bypass works like this.

A valve is placed in the location on the discharge side of the pump.

A tee is placed before it, taking off to 25 mm diameter pipe work, and another tee is glued in after it. A 25 mm pipe is connected to the first tee.

From this first tee, we install about half the length of pipe we calculated for our main line. In this instance, we would likely install 18 metres of pipe. Not in a straight line but in a tightly controlled bundle, back and forth, forth and back, pipe and elbows to achieve a long length in a small area and the CO₂ is injected just as the take-off leaves the larger bore pipe.

[Figure code: FIG-9

Proposed title: Side-Stream CO₂ Contact Chamber (25 mm Loop)]

Not difficult to make. They are difficult to look professional. Practice a lot on this to get it right.

This is a contact chamber. Contact chambers have a lot more use than simple CO₂ dissolution. In this usage, they accelerate the flow, increase turbulence and provide a torturous path, increasing the contact time and assisting with the absorption.

This quick reference chart shows the pipe length of a 25 mm pipe and the dwell time in seconds at the stated flow rate.

| Pipe Length | Volume (L) | 30 L/min | 45 L/min | 60 L/min | 75 L/min | 88 L/min |
| --- | --- | --- | --- | --- | --- | --- |
| 18 m | 8.8 L | 17.6 s | 11.7 s | 8.8 s | 7.0 s | 6.0 s |
| 24 m | 11.8 L | 23.6 s | 15.7 s | 11.8 s | 9.4 s | 8.0 s |
| 30 m | 14.7 L | 29.4 s | 19.6 s | 14.7 s | 11.8 s | 10.0 s |

A simple working solution to getting something like the flow rates is to close the valve between the bypass legs until a pressure increase is read downstream at the pump of about 10-15kPa.

CAUTION: Do not install CO₂ injection points immediately upstream of filters, air release valves, or late in the return circuit. Undissolved gas can accumulate and vent at pool inlets. Prefer the pump eye on high-flow systems or a dedicated side-stream contact chamber.

Equally important is knowing where not to place the diffuser.

It is not good to install a CO₂ diffuser immediately in front of the filter. The issue here is that the gas may not be fully absorbed before the water slows in the filter. This can lead to the gas collecting at the top of the filter and passing through the filter's air release mechanism.

In a similar way, it is not good to install a CO₂ diffuser immediately in front of a pipe air release either.

Whenever possible, avoid installing a CO₂ diffuser later in the filtration circuit. Placing the device on the return side, after all other equipment, will likely lead to undissolved unabsorbed CO₂ bubbling up at the pool return.

Installation Complete

In the preceding chapters, we have stepped through the components and installation of the various devices required for a CO₂ dosing system.

Potentially, the physical installation is complete by this point. Start-up is the next step. However, before starting up, it is best to test the system.

Open the gas supply without any other items being started. The new lines should pressurise, and the pressure should be steady.

Walk the install, listening for hissing noises. Hissing can indicate a gas leak and is a simple step to take.

Where accessible, either by pulling back the conduit sleeving or where the fittings are exposed, brush a small amount of soapy water on each joint. If there are bubbles, this indicates a gas leak.

[Figure code: FIG-11

Proposed title: Quick CO₂ Leak Check with Soapy Water]

Only after testing and checking the installation, activate the CO₂ controller. Depending on the manufacturer, there will be a way to activate it manually. Do activate manually and repeat the soapy water test on any joints downstream of the controller.

Once the soapy water test is completed and any issues found are addressed, the complete system is ready for start-up.

Configure the chemical controller for the facility, enable automatic CO₂ control, and set the CO₂ flow meter. Start with the ball at two-thirds of the scale or use the manufacturer’s setting.

# Part 3 — Operating a CO₂ Pool

Day‑to‑Day Operation in Plain English

Here we tune gently. Hold pH within a band, trim TA with small acid doses, and cut CO2 demand by reducing aeration and wind where practical.

The ‘CO2 calculator’ is a guide, not a promise. Trust the operator’s lived experience—your best data often walks around in steel‑capped boots.

pH Control

CO2 pH control behaves differently from acid pH control.

Acid produces an immediate pH response; CO2 acts through dissolution and equilibrium. The result is control that is softer, slower, and more stable once settled. This is normal behaviour, not a fault, and it requires a different tuning mindset.

Hold a gentle band (not razor-thin). CO2 changes pH by shifting the carbonate buffer, so responses are gentler than with acids. Tune slowly and watch the pool, not just the screen.

Science behind this

CO2 lowers pH by shifting the carbonate system (H₂CO₃/HCO₃⁻). Acid adds H⁺ directly; CO2 generates H⁺ internally, so the response is softer and depends on dissolution and outgassing.

The installation is not complete simply because the physical aspects are complete.

Adjustment to the pH control is likely required. This is best done in conjunction with the operator who routinely adjusts their chemical controller.

Note: The regular operator will know more about how their pool responds than anyone else. Defer to their judgment on the following adjustments.

There is no way a book can replace the knowledge and understanding of this specific pool's response, as the regular operator knows. Always defer to their judgment.

First rule of chemical control adjustments. Don’t adjust the chemical controller.

Second rule of chemical control. If adjusting, make changes incrementally and slowly.

Third rule of chemical control. Adjust one thing at a time and record what it was before the adjustment and what it is now.

This seems counterintuitive. After all, we want to make changes to the controller settings. How can we do that without adjusting the controller settings? Well, obviously, we can’t. However, the first rule still applies, and here is how.

I am assuming the pool has been operating to this point, and we are replacing an acid-dosing pump. This will be different if the pool install is brand new and the chemical controller hasn’t been commissioned.

Before adjusting the controller settings, check the pool. Consider:

- Fountains

- Weirs

- Spray points

- Bather use

- Pool depth

Chat with the operators. Is the pool, as you see it, typical, a bit quiet or busier than usual? All these need to be considered first.

The next suggested step is to stand and watch the pH reading on the controller. If practical, it is likely worth monitoring the controller and the pool simultaneously. The intent is to observe changes in bather use and how these are reflected in the pH reading. How long before the pH changes? Is the pH more erratic or very stable? Does the controller often call for pH correction in an on/off pattern, or does it call for correction only sporadically and slowly?

After watching the controller for at least 5 minutes, preferably longer, open the controller's setpoint and review its other settings.

Many controllers are configured with a rigid control philosophy. That is, if the setpoint is 7.5, many operators will set the controller to turn on whenever the pH is above 7.5, rather than taking a more relaxed approach.

It is better if the controller allows a more flexible response. Rather than dose if the pH is above 7.5 or whatever the target is. Set the target value and allow a drift around that point. For example, assuming the local regulatory framework allows it, there is no reason the pH couldn’t be allowed to drift between 7.65 and 7.35. The upper and lower limits can likely be tuned within the pH controller's proportional integral derivative loop.

[Figure code: FIG-12

Proposed title: pH Band Control vs On/Off Tight Setpoint]

Record all the pH controller settings.

This book is not about controllers and does not detail all the various settings that could be changed. For specific controllers and how to adjust their settings, refer to the manufacturer’s documentation.

Once the pH controller is set based on the collective observations and the manufacturer's instructions. Turn the system on and let the CO₂ start to control. It would be better to wait an hour or so, watching the pH and seeing how it responds in case minor adjustments are required.

Once the pH controller is stabilised, record the following parameters:

- Free Chlorine

- Total Chlorine

- pH

- Calcium Hardness

- Total Alkalinity

- Cyanuric Acid

- Total Dissolved Solids

These can be added to the tests recorded in the before you start section. This creates a base data set for comparison.

Leave the site and return the next day. I like to attend first up in the morning and check the pH controller settings against what was recorded at the time of starting.

Complete and record another water test, with the same parameters. Pay attention to whether the total alkalinity has risen substantially (> 20 mg/L) or only marginally. This will be variable as the chlorine consumption is directly responsible for the total alkalinity increase. Consequently, a water body with a higher bathing load consuming more chlorine will contribute more hydroxide, increasing the total alkalinity more than a lower load situation.

If the facility will cooperate with you, it is helpful to ask them to include the TA reading in their log and record it once a day. This can be used in the next chapter.

Correcting Total Alkalinity

CO2 is for pH; you’ll still need small, regular acid doses to keep TA on target because hypochlorite adds base.

Science behind this

Continuous hypochlorite feed introduces hydroxide/by-product base; acid neutralises that base and pulls TA back to target. CO₂ pH control won’t neutralise those bases — you still need periodic acid for TA.

Previously, it was noted that the increase in total alkalinity is a direct result of the hydroxide produced by chlorine. It was also noted that CO₂ dosing exposes this imbalance, whereas acid masks it.

Acid is required in a pool using CO₂ for TA control, not for pH control. We use acid to reduce and manage the TA.

There are several ways to do this. For example, once a month, a large dose of acid can be added to the balance tank at the end of swimming when the water body is empty of bathers.

The method suggested here is a daily or three-times-daily correction. It is much easier to dose a corrective acid dose daily than to wait for the TA to build up higher. Some of the advantages are:

- Less acid is required for any dose

- The pH will drop when acid is added, and recovery from a smaller dose is faster

- Smaller containers and less manual handling

- The usual objective for installing CO₂ is to reduce acid on site; this method maintains that objective.

- Potential reduction of scale formation

Reminder: All alkalinity values are expressed as Total Alkalinity as CaCO₃. Apply cyanuric acid (CYA) correction to TA before using TA in any LSI calculation.

- Keep Langelier Saturation Index closer to 0 than may be possible otherwise.

- More consistent water quality day to day

- Less likely to disrupt probes and other automation

To calculate the dose, take a Total Alkalinity reading.

Note: Water bodies are imperfect circulators, and not all parts of the water will read the same TA. If taking a reading for the first time in a water body, it is a good idea to take 6 or more readings from different locations and depths and average them, rather than taking a single reading. Once the water body is better understood, one reading may suffice.

The pool volume is required.

The acid's percentage strength is required as well. This is available on the SDS, on the label, or both. If, as some acids do, the percentage is say 31-37%, take the lower percentage for calculation the first time.

Understanding “Total Alkalinity as Equivalent Calcium Carbonate”

Although it is common to refer to TA simply as Total Alkalinity, the full term used in water chemistry is Total Alkalinity expressed as equivalent calcium carbonate.

This wording often confuses, so it is worth understanding it clearly.

A helpful way to think about the phrase “as equivalent” is to imagine saying:

“The sea is as blue as the sky.”

We are not saying the sea is the sky, nor that the sky is the sea. We are saying their colours are comparable on the same scale.

Alkalinity works the same way.

We are not claiming that the water's alkalinity is due to calcium carbonate. Instead, we express all alkaline species as if they were equivalent to an amount of CaCO₃. This gives us one common unit of measurement.

In a laboratory, the individual contributors to alkalinity—primarily bicarbonate, carbonate, and hydroxide, and in some cases borate or cyanurate—can be measured separately.

However, in field water treatment, we measure them together as one combined value: Total Alkalinity (as CaCO₃).

Using CaCO₃ equivalence allows all these different anions, each with its own chemical strength, to be reported on a single, standardised scale. This is why TA can be calculated, compared, and corrected using simple equations.

Calculate Acid Dose

To calculate the dose, we need the equivalent weight for the acid we are using. Common acids ew are:

| Acid | Equivalent Weight (ew) |
| --- | --- |
| HCl Hydrochloric or Muriatic | 36.46 |
| H₂SO₄ Sulphuric or Non-Fume | 49.04 |

The ew in chemistry means the mass of a substance (in grams) that supplies 1 mole of reactive hydrogen ions (H⁺).

If using another acid, look up its equivalent weight, and this value can be swapped in the examples.

A worked example is likely the most helpful here:

Pool volume 1,300,000 litres

Total Alkalinity reading 97 mg/L

Note: If using cyanuric acid in the pool, always correct the reading before applying the numbers to the equations We are not using CYA in this pool.

Total Alkalinity target 80 mg/L

Acid strength from label 32% HCl

First, we need to work out the TA correction amount.

Total Alkalinity reading – Total Alkalinity target = Total Alkalinity correction

97 mg/L – 80 mg/L = 17 mg/L

Total Alkalinity correction = 17 mg/L

[Figure code: FIG-13

Proposed title: Daily/Three‑Daily TA Correction – Workflow]

Example A — using HCl

- EW = 36.46 (HCl)

- S = 0.32 (32% strength from label or SDS)

From the chemical suppliers' SDS look up the specific gravity for the acid. This is listed as a physical or chemical property. For HCl at 32% the SDS listed 1.16 kg/L

[FIG-29 – HCL SDS Screen Grab]

- ρ = From the SDS the Specific Gravity is 1.16 kg/L for 32%.

Factor:

The factor is worked out first.

Total alkalinity (as CaCO₃) is based on equivalents:

- 50.045 g of CaCO₃ = 1 equivalent

Recall from the earlier explanation that TA is expressed as ‘mg/L as CaCO₃’, which is just a standard measurement convention. Using that, the equivalent weight calculation becomes:

This equation is rounded up by about 0.3%. It is not usual in science or maths to round early. However, as this book is aimed at field work, this is sufficiently accurate for the purpose.

This factor 2.28 doesn’t need to be worked out every time. It is explained here in case at some future point a different acid is used, in which case the factor would change.

Dose per litre:

To calculate the dose, we multiply the total alkalinity   correction we calculated earlier by the factor.

This gives us an amount of acid per mg/L to correct this total alkalinity level.

Total mass

The total mass is the number of kilograms of acid required. This is expressed as weight as mg/L is convertible to grams and grams to kilograms.

Volume

Then we can use the specific gravity we found from the SDS to calculate the amount of acid in millilitres.

In practical terms, this is a very small dose of acid, compared to the volume of this pool.

Example B — Same scenario but H₂SO₄

EW = 49.04 (H₂SO₄)

S = 0.28 (28% strength from label or SDS)

As in the HCl example, we go to the SD from the chemical supplier and look up the specific gravity:

[FIG-30 – NFA SDS Screen Grab]

ρ near 20 °C ≈ 1.25 kg/L (averaged)

Factor

The factor is worked out first, again.

Total alkalinity (as CaCO₃) is based on equivalents:

- 50.045 g of CaCO₃ = 1 equivalent

Recall from the earlier explanation that TA is expressed as ‘mg/L as CaCO₃’, which is just a standard measurement convention. Using that, the equivalent weight calculation becomes:

Dose per litre

To calculate the dose, we simply multiply the factor by the TA correction amount. So, using the 17 mg/L we are correcting for it becomes:

Total Mass

To calculate the mass, we need in kilograms we multiply the dose per litre by the number of litres in the pool and divide

This is the amount of acid in kilograms. But this acid is a liquid. So, we need to convert weight to litres.

Convert kg to litres

To work from weight to litres, we need the specific gravity. This can be thought of as the amount a litre of acid weighs in kilograms. Because of this, we can use this to convert kilograms to litres.

The acid dose required for this pool volume to correct 17 mg/L of total alkalinity is 62 litres. Compared to the volume of the pool, this is a very small dose of acid.

How to Dose the Acid

There are several options for how the calculated dose of acid can be applied. For instance:

- Pour the required amount directly into the gutter or balance tank.

- Dose using a dosing pump.

- Set up a venturi and measure the amount of acid into a container, and transfer to the pool via the venturi.

- Perhaps some other way I haven’t listed.

Of these, the dosing pump is most likely the best choice. With the dosing pump, it is possible to add the acid in a more controlled manner and increase the safety of the operator.

To reduce the possibility of overdose, it may be practical to fit or fill a drum with a specific volume. Dosing pumps are not infallible, and whilst the suggestions presented will help, they cannot stop a timer malfunction or a dosing pump error.

- After the last bathers have left the pool

- Set up the amount of acid using appropriate safety procedures.

- Set a timer to manage the dosing pump based on the calculated dose.

For example, using HCl, we calculated that we needed 43.5 L of acid. If the dosing pump is rated at 15 litres per hour, this is 45/15 = 3 hours. So, 3 hours is likely a safe dosing time.

- Set the drum or add the volume calculated plus a margin to assist keep prime to the pump.

Again, using our example, if we set up 60 litres, then the most that could be dosed is 60 litres. Given our target of 80 mg/L TA, this would give a safety buffer to prevent the pH from crashing too low overnight, should the dosing system overshoot.

- Start-up dosing pump and check by observation that it is dosing correctly.

Note: Depending on how the injection system is set up, it may necessitate isolation of the chemical probes overnight. However, as the amount of acid being added is small compared to volume, if the acid is added slowly, it is unlikely any spiking will occur. This can only be assessed by a trained professional familiar with dosing control systems on the site.

Minimising Consumption

Anything that splashes, blows air, or adds wind throws CO₂ away. Reduce aeration/wind, raise pH a touch, and lower TA to cut gas use.

Science behind this

Any increase in surface area or shear (fountains, blowers, wind) increases CO2 loss by gas exchange. Less outgassing = less CO2 you need to feed for the same pH band.

One of the criticisms of carbon dioxide gas is its consumption rate.

Whilst controlling the total alkalinity will largely deal with this, other steps can be taken to reduce usage rates.

[Figure code: FIG-14

Proposed title: CO₂ Consumption Reduction Matrix]

Reduce aeration

CO2 leaves the pool via gas exchange at the surface naturally. This is termed gaseous interchange and is a normal part of how water works.

Anything that increases aeration of the water, such as:

- Fountains

- Blowers

- Splashing

- Sprays

- Tipping buckets

- Water slides

- And many more

Will increase the aeration of the water. The aeration is effectively increasing the surface area of the water body, and this, in turn, passes more gas off the water, creating additional CO2 demand.

Whilst an ideal water body would be a still lake like placid water body using skimmer boxes rather than wet deck grates, it is not likely to be realistic.

Water bodies are supposed to be fun, used and welcoming to all. There needs to be a compromise between what is ideal for gas consumption and what the water body delivers.

Suggestions to consider will depend on the water body, its patrons and its use.

Perhaps a series of sprays and tipping buckets in the toddler pool could have a timer fitted so they are only active from 9.30 am to noon during the week, as this is the time this pool is used the most.

Staying with the toddler pool example above. If the patron use is not fixed by time, perhaps consider adding a push button activation instead. Push this button for 12 minutes of play, for example, maybe effective.

If water slides are fitted, there may be little point in them running during the week. Or perhaps they only need to run outside of school hours?

There are likely a lot of small improvements that could be made to assist with reducing gas demand and loss.

Use of Cover

As the gaseous interchange occurs at the surface of the water body, it is best to use covers when not in use. A cover will dramatically improve the gas retention, and this, in turn, will reduce demand.

However, when doing overnight acid correction, it is best to leave the covers off, as we want the gas to pass off on those nights.

Reduce wind

It's tempting to read the heading and skip this section. Indoor water bodies have wind, too.

Minimise any air blowing directly onto or across the surface. This may conflict with the air-handling unit's requirements for chloramine reduction. This is not what is suggested.

Outside of chloramine removal, air should not be directed across the water surface. If possible, add windbreaks if outside; inside, consider alternative diffusers and similar measures.

Note: For indoor facilities, a trained HVAC professional familiar with chloramine handling must be consulted before making any adjustments to the existing systems.

Decrease temperature

Hotter water dissolves the gas into it faster. However, hotter water will also pass more gas out to the atmosphere.

Consider lowering the water temperature. Generally, most people won't notice a 0.5°C change if the adjustment is made over several weeks. Perhaps consider lowering the temperature target by 0.1 degrees per week.

Raise pH

Inherently, a water body with a lower pH contains more dissolved CO2. This means that raising the pH of the water will result in less dissolved CO2. If there is less dissolved CO2, then there is less gas to pass off and less gas to replace.

If the regulated pH range is 7.2–7.8, then allowing the pH to drop below 7.7 is fine. Always maintain pH within the regulatory levels as these are often checked.

Lower TA target

It is possible to reduce TA significantly below industry norms. There is a lot involved in this discussion; suffice it to say, a TA of 30 mg/L will require significantly less CO2 than a TA of 80 mg/L. For more information on this subject, please refer to the appendix on LSI and Henry's law.

Reduce chlorine levels

As the primary source of hydroxide in water, anything that reduces chlorine demand and levels will help reduce CO2. use.

If the regulated range for free chlorine is 3.0–8.0 mg/L, consider a 3.5 mg/L target rather than 4.0 mg/L. Alternatively, as suggested for pH control, consider allowing the chlorine to vary within a range, say 3.5 to 4.5 mg/L. A more relaxed range may assist with both compliance and CO2 reduction. use.

pH Controller Setting

Please refer to the previous  Chapter 18, pH control.

Reduce Surface Disturbance

Humans will disturb the water's surface. Whilst an ideal situation would be to ban all humans and let the water body self-manage, it is unlikely to happen. Honestly, I don’t know why? We spend all this time making a perfect water body for those pesky bathers to come along and mess it up.

Anything that can be done realistically to reduce surface disturbance will improve the efficiency of CO2 consumption.

Plant Maintenance

So far in this list, the points raised have largely been intuitive. This point is less so.

Cavitation in the pump, whilst not good for a pump, may not be obvious as a gas consumer; however, this is one example.

Air leaks into the system will encourage gaseous interchange, and this will cause CO2 to leave as well.

Leaking air release valves.

Changes to the system may result in gas being bled off before it has had a chance to dissolve.

Plant maintenance is seldom connected to chemical consumption; however, it often is.

CO2 Consumption Calculator

Start with the chlorine feed as the driver, then allow for real‑world losses. Treat the number as a guide, not a promise. Actual consumption measurements on site outrank this calculator. No book can account for the specific set-up of the water body in question.

In this book, we have shown the installation steps, the start-up, discussed total alkalinity control and broadly covered ideas on minimising consumption. However, so far, we haven’t shown what good consumption looks like. Is a kilogram a day or a week too much or too little?

The best way to explore this is to show a working example.

Assumptions

These are the assumptions being used for this example.

Pool volume: 1,300,000 litres

Chlorine: maintain 4.0 mg/L target, with a loss of 1.0 mg/L per hour (so we keep feeding to hold 4 mg/L, a real pool wouldn’t be this neat, however, it is useful for demonstration)

Chlorine donor: Sodium Hypochlorite 12.5%

pH band: 7.4 to 7.7

Total Alkalinity: 80 mg/L as CaCO₃

CO2 injection efficiency: 50% (only that fraction dissolves and reacts)

Average aeration/turbulence (we’ll treat this as “typical” and already reflected by your low injection efficiency)

How Sodium Hypochlorite Increases pH

Sodium hypochlorite contains hydroxide. The hydroxide is added to assist with shelf life. Without the hydroxide, the solution would rapidly lose strength, substantially reducing the impact.

In addition to the small amount of hydroxide, the solution contains the chemical reaction of sodium hypochlorite, which creates hydroxide.

NaOCl + H2O → HOCl + NaOH

Sodium Hypochlorite + Water → Hypochlorous acid + Sodium Hydroxide

The sodium hydroxide increases both the pH and the total alkalinity. A rule of thumb is

- Each 1 mg/L of free chlorine added increases alkalinity by about 0.6–0.8 mg/L (as CaCO₃).

- To neutralise 1 mg/L of alkalinity (as CaCO₃), you need about 0.88 mg/L of CO2.

Therefore, CO2 required per 1 mg/L chlorine is:

0.6–0.8 mg/L alkalinity × 0.88 mg/L CO₂ per mg/L alkalinity = 0.6204 mg/L CO2

For this 0.6204 mg/L stoichiometric reference value (no losses, no dynamics), we round to 0.62 mg/L; that's what we’ll use below.

The 0.62 conversion assumes sodium hypochlorite. For calcium hypochlorite, use 0.71. For other chlorine sources, consult the supplier's chemistry data.

[Figure code: FIG-15

Proposed title: From Chlorine Feed to Daily CO₂ Need]

Daily chlorine loss → daily CO2 need (chemical equivalence)

Chlorine loss rate:

- mg/L per hour × 24 hours per day = 24.0 mg/L per day consumption

Note: Remember, in our example, we are setting this as a base consumption. To measure the consumption of your water body, assuming a bulk storage tank. - Place a tape on the sight glass at the level of the sodium hypochlorite. Note the date and time. - The following day, as close to the same time, place a tape at the level of the sodium hypochlorite. Record this date and time. - Repeat the step above for several days or perhaps weeks. - Measure the distance between each tape. This can be used with the tank diameter to calculate the daily volume of chlorine used. Average the daily figures, and this should provide a reasonable guide as to chlorine use.

How much CO2 is needed at the water (chemical basis) to offset that hypochlorite effect:

24.0 mg/L chlorine per day × 0.62 mg/L CO2 per mg/L chlorine = 14.88mg/L CO2 per day

So, the water would like to see 14.88mg/L of CO2 per day to hold pH steady within the band while feeding liquid chlorine to maintain 4.0 mg/L.

Convert mg/L to kilograms per day for our pool from assumptions. Pool volume: 1,300,000 litres

Total CO2 mass per day at 100% dissolution:

14.88mg/L × 1,300,000 litres = 19,344,000 mg per day

There are 1,000,000 milligrams in 1 kilogram. We simply divide:

19,344,000 / 1,000,000  = 19.344 kg

At perfect dissolution and zero losses, the pool will need 19.344 kg of CO₂ per day (chemical requirement).

Account for CO₂ Injection Efficiency

The injection efficiency will vary across our assumptions; we listed 50% as the default. This is based on an LP ceramic diffuser. That means only 50% of the CO2 gas you feed dissolves and reacts; 50% is effectively lost (blows off or bypasses). This is probably a pessimistic view; however, I would rather overestimate.

Therefore, to achieve the 19.344 kg per day chemical need, we need to allow for the losses

Chemical need ÷ Efficiency = Delivered gas per day

19.344 kg per day / 0.50 =  38.688 kg per day

Daily CO2 gas feed estimate (at 50% efficiency)  ≈ 38.688 kg per day

[Figure code: FIG-16

Proposed title: Relative Dissolution Efficiency by Diffuser Type]

| Diffuser Type | Typical CO₂ Dissolution Efficiency | Notes (Real-World Behaviour) |
| --- | --- | --- |
| LP Ceramic (Low-pressure ceramic disc/ | 35% – 55% | Produces moderately fine bubbles. Very dependent on placement; performs best in low-turbulence side stream contactors. |
| HP Ceramic (High-pressure micron | 60% – 85% | Excellent gas transfer. True “fine-pore” ceramics can exceed 80% if submerged at depth with low turbulence. Ideal for CO2. |
| Venturi Injector | 20% – 35% | Good mixing, but coarse bubble size and minimal contact time in most pool plumbing. |
| Membrane Diffuser (EPDM or PTFE) | 40% – 70% | Bubble size varies with pressure and membrane age. New membranes perform closer to 70%. Good compromise between performance and maintenance. |
| Sintered Stainless Diffuser | 50% – 75% | Produces very fine and consistent bubbles. Performs best when operated at stable pressure above ~2 bar. Durable and stable efficiency. |

Summary

Accurately predicting CO2 consumption is difficult. Some variables simply can't be accounted for in the math model.

Differences in minor chemical components within the fill water, frequency of backwashing (or, in some cases, its absence), differences in chemical controllers’ algorithms, temperature, and bather usage are all variables that are not modelled. Any of these, or a combination of them, can influence gas use. Perhaps it is better to deliberately overestimate the likely consumption than try to get it accurate. At best, this is a guide, not a guarantee.

Glossary

### CO₂

Carbon dioxide; used as a pH control agent in commercial pools.

### pH

A measure of acidity/alkalinity; critical for swimmer comfort and chemical balance.

### Total Alkalinity

Water’s ability to buffer pH changes, expressed as mg/L CaCO3.

### Calcium Hardness

Concentration of dissolved calcium; influences scaling and corrosion.

### LSI

Langelier Saturation Index; indicates scaling or corrosive tendency.

### Hypochlorite

A chlorine compound (e.g., sodium hypochlorite) used for disinfection.

### Diffuser

Device introducing CO₂ into water as fine bubbles for absorption.

### Venturi Injector

A device that draws in gas using pressure differential.

### Bypass Contact Chamber

A side stream loop used to provide longer CO₂ absorption time.

### Specific Gravity

Ratio comparing the density of a substance to water.

### Equivalent Weight

Mass of a substance that supplies one mole of reactive ions.

### Henry’s Law

Law describing gas solubility in liquids based on partial pressure.

### Regulator

Device controlling gas pressure from CO₂ cylinders or bulk storage.

### Aeration

Introduction of air that accelerates CO₂ loss and raises pH.

### Turbulence

Water motion that increases gas exchange and pH rise.

# Part 4 — Understanding the Science

Why the Science Matters (But Stays Practical)

These notes on LSI and Henry’s Law explain why the earlier advice works.

Read them when you want.

When time allows, come back—understanding how gas leaves water and how calcium balance behaves will save you money and arguments.

Appendix: Langelier Saturation Index

Quick take — LSI balances calcium carbonate. You can meet LSI and still run lower TA to reduce CO₂ demand if surfaces and local rules allow.

From my early training, I believed we were using the Langelier Saturation Index. The belief was so rife in the industry to cause near physical fights at trade nights if someone mentioned a different water balance than you.

I later found that we weren't using LSI, but rather some derivative of it.

Nearly all LSIs used in our industry are derived from, rather than, the Langelier Saturation Index.

As first developed, the LSI is a Calcite Saturation index. The index balances the calcium carbonate in the solution, so it is neither scaling nor aggressive. Since its initial publication, several modifications have been made to enhance its applicability to pool and spa water treatment. However, in addition to these changes, various companies and other interested parties have made simplified versions to suit their own needs. More recently, with the rise in app usage, a myriad of different and, in many cases, unknown calculations are occurring.

In essence, the LSI, if negative, indicates that water will dissolve calcium carbonate (). Conversely, if the LSI is positive, it indicates that calcium carbonate can form scale. At zero, the potential for scaling is neutralised; however, temperature or evaporation can change this reading.

I noticed several methods for calculating the LSI. The pool industry tends to favour one that includes an allowance for the total dissolved solids at an assumed value of 1000 mg/l.

The other standard view of the LSI for the pool industry is some version of the following:

SI = pH + Temp. Factor (TF) + CH Factor (CF) + TA Factor (AF) - 12.1.

| Temp (0C) | TF | Total Alkalinity | AF | Calcium Hardness | CF |
| --- | --- | --- | --- | --- | --- |
| 0 | 0 | 5 | 0.7 | 5 | 0.3 |
| 3 | 0.1 | 25 | 1.4 | 25 | 1 |
| 8 | 0.2 | 50 | 1.7 | 50 | 1.3 |
| 12 | 0.3 | 75 | 1.9 | 75 | 1.5 |
| 16 | 0.4 | 100 | 2 | 100 | 1.6 |
| 19 | 0.5 | 150 | 2.2 | 150 | 1.8 |
| 24 | 0.6 | 200 | 2.3 | 200 | 1.9 |
| 29 | 0.7 | 300 | 2.5 | 300 | 2.1 |
| 32 | 0.8 | 400 | 2.6 | 400 | 2.3 |
| 41 | 0.9 | 800 | 2.9 | 800 | 2.5 |
| 51 | 1 | 1000 | 3 | 1000 | 2.6 |

This equation could be simplified further by using 24 degrees as a constant. It becomes:

SI = pH + CH Factor (CF) + TA Factor (AF) – 11.5

This demonstrates one central issue with the LSI. It has become so widespread that shortcuts are possible, as I have shown. Understanding what happens inside computers or apps can be challenging when calculating the LSI value.

In demonstrating this, I am ignoring the further complication of cyanuric acid and its impact on the total alkalinity reading.

Clarification: At higher CYA levels, this becomes important, so in residential Trichlor pools, where the CYA can get high. This may be critical.

The point is that, in my early days in the pool industry, the temperature was often overlooked when discussing LSI. The argument, which has some validity, is that the change in water temperature is both prolonged and small and can be ignored. (Our temperature wouldn’t vary more than 18 degrees Celsius in the local market from summer to winter). When you look closer, you realise this is true as the temperature rises. After all, the temperature factor changes only marginally between 29 and 34 degrees; an increase of 5 degrees represents 0.1, and therefore will be slightly out, given a target of between 0.5 and -0.5. The difference between, say, 30 and 10 degrees is -0.3, which could significantly impact the calculations and would be increasing in importance for some surfaces, such as plaster.

I don't like the tombstone approach of the chart above. It is too easy to read this; however, I want to.

For example, to achieve an SI of 0 (+/- 0.5) I can use:

pH of 7.5 and CH of 75 mg/l with a TA of 300 mg/l at 24 degrees

As in:

SI = 7.5 + 0.6 + 1.5 + 2.5 - 12.1

Likewise, I can use the following:

pH of 7.6 and CH of 800 mg/l with a TA of 25 mg/l at 24 degrees

As in:

SI = 7.6 + 0.6 + 2.5 + 1.4 - 12.1

According to the chart, both are balanced. However, the first model will be challenging to hold a stable pH. The second would likely work reasonably well, although purists may suggest it will be corrosive.

This section of the discussion demonstrates that the numbers are not fixed; they are flexible. The water must not remain within a magical number range to achieve LSI or SI.

In today's world, with advancements in materials, it is unlikely that many commercial pools are still painted with chlorinated rubber. Likewise, plain plaster pools are less common for commercial water body finishes.

Clarification: Plaster pools are very common in the U.S for commercial and public pools.

Finishes such as fibreglass and vinyl in their various forms, epoxy coatings, tiles using polymer-based grouts, and similar engineered products need not be as highly mindful of the LSI and SI. They are less critical than they were 15 or 20 years ago.

Concerns about low total alkalinity levels without balanced LSI or SI are not my message.

However, a balanced pool with calcium hardness compensating for lower levels than traditional total alkalinity levels won't have as significant a negative outcome as may have been the case in the past.

Consider this for interest. In 1989, or thereabouts, I was asked to repair an older pool in the area where I was working. The pool was built simultaneously and likely by the same company that installed school pools, which must have been installed in the mid-to-late 1960s. As a result, this pool was huge, being two ends of a 33-yard pool, perhaps with four or five lanes, dropped in a backyard, joined up, and plumbed…in copper. Yes, this pool had copper pipe. Running very low total alkalinity may have occasionally resulted in low pH, which could have damaged this pool's pipework.

In another pool I worked on, the water turned green with the addition of sodium hypochlorite dosing. This is an indicator of iron in the water, which used to occur as some pools in the past were constructed using steel pipes.

We would need help finding a current pool constructed with steel pipe works. Unless perhaps some of the artificial lakes in wealthy areas of the world, however, I suspect we would struggle to find steel pipes even there.

Filters are occasionally made of stainless steel, usually coated to prevent chloride attack and thus inert. Most systems are made of inert materials such as plastics, fibreglass, titanium, and ceramics. Even cast-iron pumps are commonly coated with various coatings to reduce corrosion.

If the water body uses atmospheric gas heaters where the copper or cupronickel heat exchanger is directly exposed to the pool water, there may be an increased expectation of additional corrosion if the total alkalinity is run lower and the calcium hardness is high. The expectation may be there, however, if pH is correctly controlled, experience has shown it doesn't happen.

Let's go back and look again at what the Langelier Saturation Index is. The index is intended to balance the calcium carbonate in the solution, so the water is neither scaling nor aggressive to grout or plaster. It is often applied to metals as well.

It is imperative to realise the total alkalinity must be adjusted below the calcium hardness before lifting the calcium hardness level.

Appendix: Henrys Law.

Warmer, agitated water dumps CO2 to air, so pH rises. Less turbulence and a cover at rest keep CO2 (and pH) steadier.

In pools this explains why aeration makes pH rise.

In the previous chapter, we discussed the Langelier Saturation Index. This could be said to be the chemical side of the pool industry.

However, as mentioned, water treatment is not purely chemical. It is also partly physics. Some physics is simply unavoidable. Henry's Law states that the amount of gas that dissolves in a liquid is directly proportional to the partial pressure of that gas above the liquid at a constant temperature. Henry's Law is a scientific law. Before continuing, how many scientific laws can you recall?

So why is this a Law and not a theory? Henry's Law is considered a law because:

- It describes a fundamental physical relationship between the solubility of a gas in a liquid.

- The relationship between gas and liquid has been empirically observed and verified under various conditions.

- The relationship holds for many liquids and gases.

Due to these points, Henry's Law is considered a fundamental law of physics.

A theory is more tentative than a Law.

The following is from Masterclass:

"A scientific law might explain the relationship between two specific forces or between two changing substances in a chemical reaction. Theories are typically more expansive, focusing on the how and why of natural phenomena. Both scientific laws and theories are considered scientific fact. However, theories and laws can be disproven when new evidence emerges."

We see Henry's Law in the regularly visited or managed water bodies.

Henry’s Law is:

Where:

C is the concentration of the gas in the liquid (usually in mol/L or Molarity).

k is Henry's constant, specific to a particular gas and solvent at a given temperature.

P is the partial pressure of the gas above the liquid (usually in atm or bar).

For carbon dioxide gas, this can be expressed as:

3.4 × 10⁻² = 0.034 = [CO₂(aq)] / [CO₂(g)]

The aqueous is measured in moles/litre (molarity) and the gas in atmospheric partial pressure.

Currently, atmospheric carbon dioxide (is around 422-426 ppm (parts per million by volume) or:

4.12 x 10-4

So, at 25 degrees, the equilibrium concentration of carbon dioxide in water would be:

4.12 x 10-4 x 0.034 = 1.4 x 10-5

Henry's Law can easily be demonstrated using a spa with an air blower or a similar water body.

- Using the spa, balance the water to a more traditional water balance, with a calcium hardness of 200 mg/l and a Total Alkalinity of 110 mg/l, and adjust the pH to a range of 7.2-7.6.

- Turn off any chemical control or chemical feed systems.

- Go out to the spa and measure the pH. Write this pH down.

- Turn the blower on and, if fitted, the jet booster pump.

- Wait for 15 to 20 minutes with both running.

- Measure the pH. It has risen.

[Figure code: FIG-17

Proposed title: Spa Aeration Test – pH Rise via CO₂ Outgassing]

In the test we conducted, the spa we used was well aerated, and we achieved a rise from 7.5 to over 8.2 in 15 minutes.

This will occur in all situations, although the pH rise may not be as much as we saw in our test. It will vary according to the blower's aggressiveness and the booster pump's agitation.

The underlying reason for the pH rise is the discharge of carbon dioxide gas into the atmosphere. The water is releasing its carbon dioxide content into the air.

Other places we see this around water bodies include:

- Fountains and sprays.

- Weir edges.

- Spillovers or cascades.

- Anywhere the water is subject to turbulence and aeration.

Henry's Law states that the amount of gas that dissolves in a liquid is directly proportional to the partial pressure of that gas above the liquid at a constant temperature.

But where did the carbon dioxide come from?

[Figure code: FIG-18

Proposed title: Sources of CO₂ in Pool Water]

At current atmospheric CO2 (~400–420 ppm), air-equilibrated freshwater contains about 0.5–0.6 mg/L of dissolved CO2 near 25–29 °C; this is not alkalinity.

Total Alkalinity (as CaCO₃) at ~pH 7.5 arises mainly from bicarbonate/carbonate in freshwater and, in low-mineral water at air equilibrium, is only on the order of a few mg/L (≈2–3 mg/L as CaCO₃), unless geology adds more buffer.

We make it with the chemicals we add. It's part of the underlying chemistry.

One formula for estimating carbon dioxide content in water is:

CO2 = (TA x 2) x 10(6.2-pH)

Unravelling this equation, total alkalinity is multiplied by 2, all of which is multiplied by 10 to the power of 6.2 minus pH. Henry's Law states that the amount of dissolved. CO2 in water is directly proportional to the partial pressure of CO2 in the air.

In other words, as we use acid to lower pH, what we are doing is:

HCl + NaHCO3 = NaCl + H2O + CO2

Adding hydrochloric or muriatic acid to sodium bicarbonate to create a salt, sodium chloride (same as on your French fries), dihydrogen oxide (water) and carbon dioxide gas. The carbon dioxide gas is slowly liberated into the atmosphere.

Note that the liberation of carbon dioxide from water is a constant process. It happens all the time. However, the higher the total alkalinity and the lower the pH, the higher the carbon dioxide concentration, the faster the initial off-gassing will occur, and the faster the pH will rise.

There is a time when we can see this in action in the water body.

If you add acid to bicarbonate-buffered pool water, the acid converts bicarbonate to carbonic acid and then to CO2(aq); right in that mixing cloud, CO2 becomes supersaturated and visibly effervesces as CO2 bubbles until it re-equilibrates with air (Henry’s law). By contrast, when bubbles appear from warming or gentle degassing without fresh acid, the escaping gas is mostly nitrogen and oxygen, because their equilibrium concentrations in air-equilibrated water are much larger than CO2 at the same temperature and pressure.

Every water body contains carbon dioxide. It is a simple fact.

The carbon dioxide will slowly escape from the water body, and as it does so, the pH will rise. The more carbon dioxide is present in the water, the faster the pH will rise. Conversely, the higher the total alkalinity, the more carbon dioxide is required to maintain a stable pH.

This is why using a water balance with a total alkalinity of 100 mg/l and trying to maintain a pH of 7.5 using an acid pH control—results in an ongoing demand for acid and bicarbonate one after another.

HCl + NaHCO3 = CO2 + H₂O + NaCl

So, Acid + Bicarbonate = Carbon Dioxide + Water + Salt

An understanding of Henry's Law is required to understand carbon dioxide pH control.

This chapter discusses that water body treatment is not just chemistry. As the water body is part of the environment, it is also subject to physics. To consider one without the other is not practical. We also explained an experiment that is simple to conduct in the real world to demonstrate Henry's Law and its impact. In the experiment, we accelerate the off gassing by using the blower.

We then discussed chemistry and explained where carbon dioxide is made in every water body.

Any real chemists reading this, please remember that I am primarily self-taught, with some help. There was no formal training available in my early years.

Henry's Law Meet Langelier Saturation Index

In the previous few chapters, we discussed Langelier Saturation Index and Henry's Law as separate topics.

This is because they are best addressed separately before we attempt to bring them together.

We could leave them separate, and I likely would on a vinyl or fibreglass surface domestic water body.

In the commercial world, there are considerations—manufacturers' warranties, bather comfort, health inspectors, and so on. In my opinion, it would be better to merge our understanding.

Typically, health authorities recommend a pH level between 7.2 and 7.8. This may vary slightly. However, this is generally the documented range.

Generally, the pool industry suggests a range of between 7.4 and 7.6 based on the chlorine activity range. With 7.5 often referred to as ideal.

For this discussion, I will stick with 7.5.

Going back to one of the examples from our discussion on Langelier

pH of 7.6 and CH of 800 mg/l with a TA of 25 mg/l at 24 degrees

As in:

SI = 7.6 + 0.6 + 2.5 + 1.4 - 12.1

But I want a pH of 7.5.

Let's lower the CH to, say, 500 mg/l. We can approximate this to be a 2.4 factor, as it's not documented in the table.

SI= 7.5 + 0.6 + 2.4 + 1.4–12.1

It yields an SI of -0.74, indicating that it is much more likely to dissolve calcium carbonate than we would like.

So, let's raise the total alkalinity. Let's use 50 mg/l as a target.

Therefore, the CH is 500 mg/L with a TA of 50 mg/L at 24°C with a pH of 7.5.

SI= 7.5 + 0.6 + 2.4 + 1.7–12.1

Now, with a slight adjustment of TA, we have gone from an aggressive situation to a positive index.

It is vital to realise that the total alkalinity must be adjusted below the calcium hardness before lifting the calcium hardness level.

How does this help with Henry's Law?

Natural freshwater bodies, such as streams and lakes, often have a neutral or near-neutral pH, typically around 7.00. The pH changes and variations depend on the source, as the water encounters minerals and rolls through the environment, which can result in far different pH readings. However, for discussion, let's work on 7.0.

The total alkalinity levels in these natural surface waters typically range from 30 to 40 mg/L. (I do know there are exceptions; this is a generalisation)

Why is a swimming pool any different?

Why can't a swimming pool function like natural, fresh surface water containing a total alkalinity of 30 to 40 mg/L? Does Langelier stop us?

In contrast, using the same maths, the theoretical pH of the natural water would be lower than its actual pH. It's unlikely this water's pH would rise.

However, all our training, experience, and expertise. As well as all the industry discussions and talks suggest a total alkalinity of 30 mg/l is too low…After all, the Langelier Saturation Index will be too low. The water will be aggressive, and it will stop us.

Does it?

Look again.

All the following are balanced with SI:

SI = pH + Temp. Factor (TF) + CH Factor (CF) + TA Factor (AF) - 12.1.

| Temp C | CH | TA | pH | SI |
| --- | --- | --- | --- | --- |
| 24 | 150 | 150 | 7.6 | -0.44 |
| 12 | 200 | 150 | 7.8 | -0.1 |
| 34 | 500 | 25 | 7.5 | 0.0 |
| 24 | 500 | 25 | 7.5 | -0.2 |

All of these water balances apply to the SI equation. All are within the +/-0.5 tolerance and are perfectly reasonable for maintaining a water balance.

However, only one will have a pH that moves very slowly, with a TA of 25 mg/L. I prefer a slightly higher TA; however, this is an excellent demonstration to drive home the point.

Please note that local regulations may require a minimum TA. Always defer to your local requirements.

It is possible to meet both the requirements of Langelier and, simultaneously, work on Henry's Law in a water body. It isn't against everything you know. It's uncomfortable to think this far through against what you previously believed.

It's okay, and the point is made. The LSI and Henry's Law can work together, allowing us to manipulate the water balance and prevent damage while meeting normal industry expectations.

# Part 5 — Technical Appendices & Tools

Quick Reference and Extras

This is the toolbox—worked maths, painting tips for conduit, checklists and start‑up steps you can photocopy.

The aim is repeatable results. If your site differs, make a note next to the checklist line and keep going.

Appendix: Calculating Tube Size Example

A longer/thinner tube slows flow. Bigger ID and shorter runs give you more, steadier gas delivery at the same pressure.

This calculation is advanced and intended for advanced installer use. Feel free to skip it if you like.

Don’t worry too much about the details of these equations. In the pool industry, we often say, “It’s not rocket science.”

Tube flow calculations are the same compressible-flow equations used in rocket nozzle design. In this case, it is.

Assumptions we will use for examples:

- Room temperature is steady (about 20–25 °C).

- Straight, horizontal run of tube (about 30 m).

- Smooth plastic tube (nylon/PU/PE).

- Outlet is near atmospheric pressure (suction side).

- Regulator is set somewhere around 200–300kPa gauge (add ~101kPa to get absolute).

[Figure code: FIG-19

Proposed title: Roadmap: 9 Steps to Estimate CO₂ Tube Flow]

Step 1 — Area from tube size

Use the inside diameter (ID). Convert mm to metres, then area A = (pi × D2) / 4.

Example IDs:

6×4 → D = 4 mm

8×5 → D = 5 mm

10×6.5 → D = 6.5 mm

To convert to metres, simply divide by 1000 (there are 1000 mm in a metre), for example:

4 mm / 1000 = 0.004 metres

A = (pi x 0.0042) / 4

A = (pi x 0.000016) / 4

A=pi x 0.000004 / 4

A = 0.000012566370614 m²

For the worked example, we’ll use 8×5 mm (ID = 5 mm), therefore we will run this maths again to clarify how it works:

5 mm / 1000 = 0.005 metres

A = (pi x 0.0052) / 4

A = (pi x 0.000025) / 4

A=0.0000785398163375 / 4

A = 0.000019634954084375 m²

Step 2 — Pressures we will use

Convert your regulator setting from kPa gauge to Pa absolute by adding atmospheric pressure (about 101,325 Pa).

Example:

250kPa gauge → 250,000 Pa. Add 101,325 Pa → P1 ≈ 351,325 Pa.

For the discharge, a diffuser is required. Whilst diffusers are covered in part 2, Chapter 15 Injection Point, the chart below lays out typical diffusers and the pressure required to drive them.

| Diffuser/Injector | Gas side Pressure Required at Diffuser (typical) bar | Gas side Pressure Required at Diffuser (typical) kPa | Pressure Required at Outlet (With atmospheric added) Pa |
| --- | --- | --- | --- |
| Ceramic micro-bubble LP grade | 0.3-1.0 | 30-100 | 201,325 |
| Ceramic micro-bubble HP grade | 1.0-2.0 | 100-200 | 301,325 |
| Venturi Injector | ~20–30% ΔP | ~20–30% ΔP | ~20–30% ΔP |
| Membrane dis/tube (EPDM/PTFE-coated EPDM) | 0.1-0.3 | 10-30 | 131,325 |
| Sintered metal sparger(316L) | 0.2-2.0 | 20-200 | 301,325 |

For our example, we will assume a ceramic micro bubble LP grade, making our value for:

P2 about 201,325 Pa.

Note: If doing the equations with a venturi injector, choose one of the other lower values unless the delta pressure is known.

Step 3 — Get a mean density (no stress)

You need to know how packed the gas is inside the tube. That’s its density. We work it out once at the inlet pressure and once at the outlet pressure, then take a simple average.

The only numbers you need:

- P₁ = inlet (absolute) pressure in pascals (Pa) — you already found this in Step 2 - 351,325 Pa

- P₂ = outlet (absolute) pressure in pascals (Pa) — usually ~201,325 Pa.

- T = temperature in Kelvin (K) — room temp 22 °C → 295 K (just add 273.15).

- Rₛ (for CO₂) = 188.9 J/kg·K (you can treat this as a fixed constant).

Note: To convert any temperature to K, all we do is add to our ambient temperature in Celsius. Using our example: Initial temperature becomes: 22 °C + 273.15 = 295.15 K

Use:

density = pressure ÷ (Rₛ × temperature)

which is written mathematically as:

rho = P / (Rs × T).

Worked example:

Regulator inlet pressure:

Multiply Rₛ × T

Rₛ188.9 × T 295 ≈ 55,800 for clarity labelled z

Divide P₁ by that number z

Example P₁ = 351,325 Pa from step 2

P₁351,325 ÷ z 55,80 0 ≈ 6.3 kg/m³

So, ρ₁ ≈ 6.3 kg/m³

Outlet pressure – assumed to be 0kPa as the injection point is the suction line (could be negative, but we are using 0kPa for our example)

As we are using 0kPa, we know this is one atmosphere, see step 2.

P2 is about 201,325 Pa.

P2 201,325 ÷ z 55,800 ≈ 3.6 kg/m³

Mean density (the one you’ll use)

Just average those two:

ρm = (ρ₁ + ρ₂) ÷ 2

ρm ≈ (6.3 + 3.6) ÷ 2 ≈ 4.958681394 kg/m³

What the maths is saying is:

- At the high-pressure end, the CO₂ is packed tighter (~6.3).

- At the outlet it’s looser (~3.6).

Using the average ~5.0 is good enough for our job

Tiny ready-reckoner

Use T ≈ 295 K (about 22 °C). For common regulator settings:

| Regulator kPa at gauge | P₁ absolute Pa | ρ₁ (inlet) kg/m³ | ρ₂ (outlet) kg/m³ | ρm to use |
| --- | --- | --- | --- | --- |
| 200 | 301,325 | ≈ 5.41 | ≈ 3.61 | ≈ 4.51 |
| 250 | 351,325 | ≈ 6.30 | ≈ 3.61 | ≈ 4.96 |
| 300 | 401,325 | ≈ 7.20 | ≈ 3.61 | ≈ 5.41 |

Step 4 — Friction factor f (a quick practical choice)

For a smooth plastic tube, a quick field estimate is fine. Make a simple first guess for the friction factor
Start with f = 0.02.
(This is a safe first guess; we’ll update it later.)

When we return with the updated value, we use Blasius:

f ≈ 0.3164 × Re(-0.25).

Example with Re = 34,000:

Re(-0.25) = 1 / Re(0.25)

Re(0.25) = 34,000(0.25) ≈ 14.5

Re(-0.25) ≈ 1 / 14.5 ≈ 0.069

f ≈ 0.3164 × 0.069 ≈ 0.022

Reynolds number uses your velocity, which we compute in Step 6.

We have done this with 0.02; however, later, after step 6, run again with your real Blasius line (it usually lands ~0.021–0.026).

Step 5 — Get the pressure “push” term

Compute (P12 − P22).

Example:

P1 351,325 Pa (from step 3)

P2 201,325 Pa (from step 3)

351,3252 – 201,3252 = 123,429,255,625 – 40,531,755,625 = 82,897,500,000 Pa2

This captures the effect of gas compressibility without hard maths.

Step 6 — Mass flow in one line (Corrected Isothermal Compressible Form)

The formula to apply is:

m˙ = (A/2) × sqrt(D/(fL)) × sqrt((P₁² − P₂²)/(Rₛ T))

Where:

- A is cross-sectional area (m²),

- D is internal diameter (m),

- f is Darcy friction factor (–),

- L is pipe length (m),

- P₁ and P₂ are upstream/downstream absolute pressures (Pa),

- Rₛ is the specific gas constant (J·kg⁻¹·K⁻¹),

- and T is absolute temperature (K).

We have already worked out many of these:

D = 0.005 m (from Step 1)

A = 0.000019634954084375 m² (from Step 1)

(P₁² − P₂²) = 82,897,500,000 Pa² (from Step 5)

f = 0.022 (from Step 4)

L = 30 m (assumed)

To complete the corrected calculation, we also need: Rₛ for the working gas and the line temperature T. If the gas is carbon dioxide, typical values are Rₛ ≈ 188.92 J·kg⁻¹·K⁻¹, and T is the operating absolute temperature (e.g., 293–313 K).

Rₛ ≈ 188.92 J·kg⁻¹·K⁻¹

T≈ 295.15 K (assumed)

Now we have all the components, we can start to work on them as minor equations:

(A/2) = 0.000019634954084375 / 2 = 0.0000098174770421875 m²

(f×L) = 0.022 × 30 = 0.66

D/(fL) = 0.005 / 0.66 ≈ 0.0075757576

sqrt(D/(fL)) ≈ sqrt(0.0075757576) ≈ 0.087028

sqrt(P₁² − P₂²) ≈ sqrt(82,897,500,000) ≈ 287,919.2595 Pa

(Rₛ T) = 188.92 x 295.15 = 55,759.738

Therefore, 1/√(Rₛ T) becomes

1/√(55,759.738) = 1/236.1349995235776 =0.0042348656574315

Now that we have calculated the minor components, we can assemble the maths as:

m˙ = 0.0000098174770421875 × 0.087028 × 287,919.2595 × 0.0042348656574315

m˙≈0.001041763775 kg\cdotps−1

Step 7 — Velocity (so nothing is mysterious)

Carry-forward for the example:

A =  0.000019634954084375 m² (from Step 1)

pm (mean density) ≈ 4.958681394 kg/m³ (from Step 3)

m_dot ≈ 0.001041763775 kg\cdotps−1 (from Step 6)

The formula is

v= m_dot ÷ (pm × A)

Again, break this down into smaller bits to solve and then bring them back together:

(pm × A) = 4.958681394 x 0.000019634954084375 = 0.0000973634815

(m_dot we already know, so the sum becomes)

v= 0.001041763775 ÷ 0.0000973634815 = 10.6997 m/s

Step 8 — Optional quick safety check (Mach number)

Speed of sound at room temperature:

a = sqrt( gamma × Rs × T ).

Keeping with our example:

CO₂, gamma ≈ 1.30

(Rₛ T) = 188.92 x 295.15 = 55,759.738 (from Step 6)

a = sqrt(1.3 x 55,759.738) = sqrt(72,487.6594) = 269.23 m/s

To check against the speed of sound for CO₂

Mach = v / a

Keeping with our example:

v= 10.6997 m/s (from step 7)

a=269.23 m/s (from above)

Mach = 10.6997 / 269.23 = 0.039741856405304

If Mach is well below 1 (e.g., under 0.3), you are safely subsonic, and this simple method is fine.

Step 9 — If you need standard volumetric flow to match a datasheet

Equipment manufacturers do not publish flow curves under your actual conditions. They publish ratings under standardised conditions, e.g.:

- SCFM (Standard Cubic Feet per Minute)

- SL/MIN (Standard Liters per Minute)

- Nm³/hr (Normal cubic meters per hour)

- m³/hr at STP

Therefore, it may be necessary to correct your data to get a direct comparison. To complete this, the formula to apply is:

Vdot_std = m_dot / rho_std

We have the information to complete this final check.

m_dot ≈ 0.001041763775 kg\cdotps−1 (from Step 6)

A:“Standard” at 20 °C, 1 atm (rho_std = 1.80 kg/m³)

Vdot_std = 0.001041763775 ÷ 1.80 = 0.000578757653 m³/s

Convert to L/s and L/min:
0.000578757653 m³/s = 0.5788 L/s = 34.73 L/min (SL/MIN at 20 °C)

B. “Normal” at 0 °C, 1 atm (rho_std = 1.98 kg/m³)

Vdot_N = 0.001041763775 ÷ 1.98 = 0.000526143320 m³/s

0.000526143320 m³/s x 3600 = 1.8942 m3/h (Nm³/h basis)

As manufacturers' data is often published under standardised conditions across different ambient temperatures, this table provides the values required based on typical cited temperatures.

| Temperature °C | Approximate rho_std for CO₂ kg/m3 |
| --- | --- |
| 0 | 1.96 |
| 15 | 1.86 |
| 20 | 1.83 |
| 25 | 1.80 |

Appendix Painting Plastics

Painting plastic is a somewhat frustrating task. Paint is applied, looks great, dries, and then, as soon as it's touched, picked up, or moved, the paint literally falls off in the affected section.

This happens because plastic has a layer of oils on the surface known as plasticisers. These plasticisers prevent the paint from binding to the plastic; instead, the paint binds to the plasticiser, and as this is effectively an oily coating, the paint is effectively binding to nothing.

To successfully paint plastic, the plasticisers need to be removed. There are three ways around this I am aware of:

- Heat – plastics manufacturers use flaming before printing to clear the plasticisers

- Special undercoats – Hardware stores sell undercoats that claim to prime plastic to prevent this issue.

- Chemical – Use of solvents can remove the plasticiser and provide a suitable surface.

[Figure code: FIG-20

Proposed title: How to Paint Plastic Conduit (3 Valid Methods)]

Heat can be used either as a flame or with a heat gun. The technique is to effectively heat the surface sufficiently to allow the plasticisers to float off and prepare the surface. Plastic should be painted whilst warm.

Special undercoats are likely expensive. However, it may be the best option depending on location and local regulations, safety requirements and the like. As with any chemical used on site, always obtain and retain a copy of the safety data sheet and follow this document's safety requirements.

Our current method is to use methyl ethyl ketone (MEK). It is vital to obtain, retain and read the safety data sheet on this product. Best used outside in a well-ventilated area. Don the personal protective equipment as listed in the safety data sheet. Literally wipe the conduit with the MEK, and paint is applied immediately. MEK is one of the components of PVC glue. The surface of the plastic becomes sticky when wiped, and this is what the paint is applied to. This method literally glues the paint to the plastic. Once the paint is dry, it is a lot more resistant to scrapes and scuffs. Another coat over the top, and it is going to last for years, not days.

For small-bore conduit, we normally paint it before fixing it in place. Sure, conduit can be painted once mounted, but it is fiddly and somewhat difficult.

Appendix: Installation and Commissioning Checklist

| Date |  |
| --- | --- |
| Client |  |
| Client Contact |  |
| Site |  |
| Waterbody |  |
| Volume |  |
| Temperature |  |

Water Tests

|  | Fill Water | Before Start | Start Up | Day 1 | Day 2 | Day 3 | Day 4 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Free Chlorine |  |  |  |  |  |  |  |
| Total Chlorine |  |  |  |  |  |  |  |
| pH |  |  |  |  |  |  |  |
| Calcium Hardness |  |  |  |  |  |  |  |
| Total Alkalinity |  |  |  |  |  |  |  |
| Cyanuric Acid |  |  |  |  |  |  |  |
| Total Dissolved Solids |  |  |  |  |  |  |  |

Record Settings

Use or add additional lines to suit the site.

|  | First Visit | Start Up | Day 1 | Day 3 |
| --- | --- | --- | --- | --- |
| pH Set point |  |  |  |  |
| Chlorine Set point |  |  |  |  |
| CO₂ regulator pressure |  |  |  |  |
| CO₂ Flow rate |  |  |  |  |

Appendix: Start Up Steps

Step 1 — Do Nothing (Deliberately)

Once the installation is complete and leak tested:

- Enable CO₂ control.

- Set the initial flow conservatively (manufacturer recommendation or mid-range).

- Do not immediately alter controller settings. Record settings in the form provided.

Then stand and watch.

Observe:

- How often does the controller call for correction?

- Is the pH drifting slowly or sharply?

- Does bather activity visibly affect the reading?

- Is chlorine feeding continuous or intermittent?

- Are there visible undissolved bubbles returning?

Watch for at least 20–30 minutes. Longer if practical.

The goal is not to fix. The goal is to understand.

Step 2 — Speak to the normal Operator

The regular operator knows the water body better than anyone. This is not always the centre manager; it is not necessarily the duty manager. It is the person who is usually responsible for adjusting the chemical controller.

Ask:

- Is today a typical bathing load?

- Is this chlorine feed rate normal?

- Does the pH usually move this way?

- Are we in peak or quiet season?

- Has anything recently changed?

Do not override their experience with theory.

Field knowledge outweighs first-day assumptions.

Step 3 — Record, Don’t React

Record:

- pH set point

- Control band

- Proportional / integral values (if adjustable)

- Chlorine set point

- Current CO₂ regulator pressure

These values are your baseline.

Do not change them unless the behaviour is clearly unstable.

Change slowly. Change one thing at a time. Change incrementally. Wait at least one turnover to see the reaction.

Step 4 — Allow the System to Find Its Balance

CO₂ control is softer than acid control.

Allow time for:

- Dissolution equilibrium

- Chlorine demand patterns

- Aeration effects

- Normal daily cycles

If the pH is within regulatory limits and moving predictably, leave it alone.

Small drift is not failure.

Step 5 — Return the Next Day

The real commissioning check is 24 hours later.

Return at roughly the same time of day.

Check:

- Has the pH stabilised within the band?

- Has total alkalinity risen noticeably?

- Has CO₂ consumption been excessive?

- Has the controller short-cycled?

Now, and only now, make minor adjustments if required.

Reminder: Change slowly. Change one thing at a time. Change incrementally. Wait at least one turnover to see the reaction.

Guiding Principles

- Act intentionally.

- Adjust slowly.

- Change one variable at a time.

- Trust observed behaviour over assumption.

- Defer to the operator’s lived experience.

- Never tune a system you do not yet understand.

This list is not comprehensive; it is a guide. It may be that this site needs daily visits for 3-4 days. Perhaps it needs help for a week or more. Be generous with time and appreciate that this is not an infallible fixed process.

Note: Local health codes and Authority Having Jurisdiction (AHJ) requirements supersede this guidance. Always document site-specific compliance.

Appendix: Global Standards Crosswalk for CO₂ pH Control

This section provides a comparative overview of international standards governing the use of carbon dioxide (CO₂) for pH correction in commercial aquatic facilities. It highlights whether CO₂ is permitted, outlines key requirements, and includes notes relevant to operators and regulators.

| Region / Standard | CO₂ Allowed? | Key Requirements | Notes |
| --- | --- | --- | --- |
| North America / PHTA/ICC (ANSI/APSP/ICC-1 & -2) | Yes | CO₂ permitted as pH control agent; must comply with safety, ventilation, and injector placement guidelines. | Widely used in commercial pools; referenced in CPO® Handbook. Local codes may vary. |
| Europe / BS EN 15288-1:2018 + A1:2024 | Yes (implicitly) | Focuses on safe design and operation; CO₂ not explicitly named but allowed under chemical dosing provisions. | CO₂ use must meet chemical handling and safety standards. Inspector discretion applies. |
| Germany / DIN 19643-1:2023 | Yes | CO₂ recognized for pH control; dosing must be precise and integrated with water treatment systems. | Highly technical; emphasizes process control and water quality outcomes. |
| Australia/NZ / AS/NZS 1838:2021, 1839:2021, 2783:2025 | Yes | CO₂ allowed; must meet gas safety, injector design, and water balance requirements. | Local health departments may require additional documentation or approval. |

Health Inspector Talking Points

Use the following points when discussing CO₂ pH control systems with health inspectors or regulatory authorities:

CO₂ is recognized in multiple international standards as a safe and effective pH control method.

Proper injector placement and gas dissolution techniques minimize off-gassing and ensure stable pH.

CO₂ systems reduce handling risks compared to mineral acids, improving operator safety.

Water balance can be maintained within LSI guidelines using CO₂ with adjusted alkalinity and calcium hardness.

CO₂ dosing systems can be integrated with automated controllers for precise regulation.

Facilities using CO₂ have demonstrated reduced chemical consumption and improved water quality.

Documentation of injector setup, safety protocols, and water balance calculations supports compliance.

About the Author

David Watson entered the aquatic industry by accident — quite literally. Early for a job interview at a carpet factory in Auckland, he parked outside a closed pool shop to read a book. The shop had just been broken into by an ex-business partner, and when the owner returned from the Takapuna police station, he assumed David was connected to the incident. Six and a half hours later, after a conversation that wandered from chemistry to pumps to life in general, David walked out not with a police report — but with the job offer that would shape the next forty years of his career.

David’s early education in water chemistry came from a mix of unlikely and brilliant mentors: private tuition from Ty Webb, guidance from a Henderson Environmental Health Officer, and hands-on training from Ken “the poison dwarf” of EziClor Chemicals, whose own lineage traced back to the Blue Haven School in Los Angeles. This blend of practical experience and scientific curiosity set the foundation for David’s lifelong habit of questioning assumptions, testing claims, and replacing industry folklore with real, measurable understanding.

After relocating to Western Australia, David spent over three decades with Shenton Aquatics, becoming one of the state’s most experienced specialists in recirculating aquatic systems. His work spans microbial risk mitigation, hydraulic troubleshooting, regulatory compliance, and technical innovation — including serving as a joint inventor on a U.S.-filed water chemistry dosing process. Known for turning complex chemistry and physics into practical, field-ready guidance, David’s approach has always been grounded in one belief: a pool is not a static container of water, but a dynamic system with safety as its first obligation.

Across his career, David has worked alongside some of the most capable pool technicians in the trade — people who can rebuild a pump with a shifter and a bit of swearing, ride motorbikes on the weekend, and drink him under the table without breaking a sweat. David is the opposite: bookish, early-to-bed, happiest when solving a technical puzzle, and quietly driven by a desire to lift industry professionalism through clear thinking and better understanding.

This book continues that mission. It is his attempt to bring clarity, science, and real-world practicality to a topic often misunderstood, oversimplified, or dismissed — carbon dioxide pH control. What you’ll find here isn’t theory for theory’s sake; it’s the distilled outcome of decades spent watching what happens in the water, on site, at 3 pm on a summer’s day when the toddler pool is erupting like a geyser, and the pH won’t hold still. It’s a guide written for the people who do the work, from someone who still thinks like a technician first.

### Contact and Support Information

For further assistance, technical support, or to provide feedback on this guide, please visit:

Website: www.davidwatsonpoolconsulting.com

Here you can find:

- Additional resources and downloadable forms

- Contact details for consulting and training services

- Updates and announcements related to pool water chemistry

If you require direct support, please use the contact options provided on the website to reach out to David Watson Pool Consulting.